## Schedule 1-P&G's
SARS - PROPOSED GENERATOR SETS FOR GIYANI
SCHEDULE 1 : PRELIMINARIES AND GENERAL
| Payment |  |  |  | Rate | Amount
Item | Reference | Description | Unit | Qty | (R) | (R)
1. | SABS | SCHEDULE 1:
| 1200 A | PRELIMINARY & GENERAL
1.1 | 8.3 | FIXED-CHARGE ITEMS
1.1.1 | 8.3.1 | Contractual Requirements | Sum | 1
| 8.3.2 | Establish Facilities on Site
1.1.2 | 8.3.2.1 | Facilities for the Contractor
1.1.3 |  | a Offices and storage sheds | Sum | 1
1.1.3 |  | b. Ablution and latrine facilities | Sum | 1
1.1.3 |  | c. Tools and Equipment | Sum | 1
1.1.3 |  | d. Water supplies, electric power & communication | Sum | 1
|  | e. Plant | Sum | 1
|  | f. Security of works | Sum | 1
1.1.3 | 8.3.4 | Remove Contractor's site establishment on completion | Sum | 1
1.1.4 | 8.4.0 | OPERATION AND MAINTENANCE OF FACILITIES
ON SITE
Facilities for the Contractor
|  | a) Office and storage sheds | sum | 1
|  | b) Ablution and latrine facilities | Sum | 1
|  | c) Provision of water, power and communication facilities | Sum | 1
|  | d) Tools and equipment | sum | 1
1.1.5 | 8.5 | TEMPORARY WORKS
| 8.5.1 | a) Protection of infrastructure until completion of project | Sum | 1
| 8.5.2 | Existing Services
|  | b) Excavate by hand in soft material to expose all underground services | sum | 1
1.1.6 | 8.6 | OCCUPATIONAL HEALTH AND SAFETY
|  | Risk Assessment Procedure, QM, Quality Management System, Health and Safety Specification, Environmental Plan, Safety Inspections, OHSA Appointments, Non-Conformance Process to be available in office (Payment after certification by SARS CoW that above documentation is in place, according to Sars requirements and implemented) | Sum | 1
TOTAL CARRIED TO SUMMARY

## Schedule 2, Plinth,Int.
SARS - PROPOSED GENERATOR SETS FOR GIYANI
SCHEDULE 2: PLINTH AREA CONSTRUCTION
| Payment |  |  |  | Rate | Amount
Item | Reference | Description | Unit | Qty | (R) | (R)
2.0.0 | SABS | Site Preparation
|  | a)Clearing and grubbing to 150mm depth | m2 | 24
|  | b) Provision for relocation of services | Sum | 1
2.1.0 | 1200 D | SECTION: EARTHWORKS
2.1.1 | 8.3.3 | Excavate for all foundations in all materials, and place within freehaul distance of 2km or stockpile as instructed by engineer for
|  | a) excavate for palisade beam foundations in all materials, and use for backfill or dispose for depth up to 150mm (over and above 150mm cleared after grubbing) | m³ | 1.33
|  | b) excavate for plinth in all materials up to depth of 0.2m, and use for backfill or dispose (over and above 150mm cleared after grubbing) | m³ | 2.68
|  | c) Extra over for trimming for plinth downstand beam and plinth after compacting layerworks | m³ | 1.98
|  | d) Extra over items under 2.1.0 for overhaul on material hauled in excess of a free-haul distance of 2 km for haul up to 5km | m³-km | 5.99
2.1.2 | 8.3.5 | Process base material by the following processes, as relevant and use in base (applicable to item 2.1.3)
|  | a) Stabilization | m³ | 2.68
| 8.3.8 | Stabilizing agent:
|  | b) Portland cement @ 2.5 % | t | 0.1
|  | Compaction Test | no | 2
2.1.3 |  | Construct base with stabilised gravel material (C4) from borrow pits/designated excavations or stock pile
|  | a) Prepare new surface (base) by ripping and compacting insitu material in 150mm layers of to 93% MOD AASHTO density | m³ | 3.6
|  | b) Prepare new surface by compacting in 150mm layers of C4 material to 95% MOD AASHTO density with 2.5% cement by weight for entire area inside palisade fence | m³ | 8.205
10515
2.8 |  | Paving
2.8.2 | LI | Supply and lay 60mm zig zag pavers over 20mm sand complete | m2 | 11
2.2 | SABS | SECTION: CONCRETE STRUCTURAL
1200G
2.2.1 | 8.2.1 | FORMWORK
|  | a) Rough vertical formwork to sides of plinths and beams | m2 | 11.4
Total carried Forward
Total brought Down
2.2.2 | 8.3.1 | REINFORCEMENT
a) High yield steel bars
|  | i) in plinths for stools | kg | 14
|  | ii) in beams for palisade and downstand beams | kg | 120
14.4
|  | b) Mild steel bars in downstand beams and palisade beam | kg | 110
|  | c) Ref 245 High tensile welded mesh reinforcement to: | [5 empty] | 36.6667 | 63.3333
|  | i) Plinths | m2 | 13.4 |  |  |  | 81.4 | 96
[8 empty] | 50.468 | 59.52
2.2.3 |  | CONCRETE WORKS | [5 empty] | 42.9792 | 74.2368
| 8.4.3 | a) Blinding layer
|  | Class 10MPa/19mm 50mm thick | m3 | 0.3325
|  | b) Concrete beam under palisade - Class 25MPa | m3 | 2.66
|  | c) Class 25MPa to downstand beams and plinth | m3 | 4.4939
NI |  | Slump test | no | 1
NI |  | Concrete cube test (9Cubes) for 7, 14 and 21 day tests | set | 1
2.3.0 |  | PALISADE FENCE AND GATES
2.3.1 |  | Steelwork
|  | a) Supply and fix 10 by 80x40 square hollow sections to carry vertical members as per item 2.4.0 b) including all connections and fixing onto brick piers | m | 21
|  | b) Supply and install 2.025m long vertical members for palisade with 40x40x3 angles. Members to be welded on horizontal members as per item a) | No | 83
|  | c) Supply and install 1800m wide double swing steel gate to match palisade fence. Complete with hinges connections etc | Sum | 1
2.3.2 |  | Painting to steelworks
|  | a) Priming with 1 coat red oxide | m2 | 35
|  | b) 2 coats charcoal/ grey gloss enamel paint | m2 | 70
2.3.3 |  | Masonry
|  | a) Supply & lay one brick, face work | m2 | 7 |  |  | 0.05
|  | b) Brick piers 460x345mm at centres as per drawing | m3 | 2.4757
|  | c) Plastering to achieve finish to match existing building | m2 | 28
2.4.0 |  | Other Extras
|  | New cylinder locksets for palisades | No | 1
2.5.0 |  | MECHANICAL WORKS
|  | a) Supply and Install SANS approved 9kg D.C.P (Dry Powder) fire extinguisher | No | 1
|  | b) Supply and install SANS approved 5kg aluminium CO2 (Carbon Dioxide) fire extinguisher | No | 1
Total carried Forward
Total brought Down
2.6.0 |  | SIGNAGE
|  | a) SABS approved signage for Fire extinguishers and all required statutory signs for the generator area (e.g. No smoking, no access etc) | Sum | 1
2.7.0 |  | Final commisioning of the works including removal of rubble, dust and and other waste generated during construction. | Sum | 1
TOTAL CARRIED TO SUMMARY

## Schedule 3, Electrical
SARS - PROPOSED GENERATOR SETS FOR GIYANI
SCHEDULE 3: GENERATOR INSTALLATION
Item | Description | Unit | Qty | Rate | Amount ( R )
PRIME RATED GENERATOR INSTALLATION
SCHEDULE 1: GENERATOR INSTALLATION
A | Supply, deliver to site, off-load and store on site as required a prime rated 200 kVA diesel generator set as specified, scheduled and shown on the drawings, including all materials, exhaust system, automatic mains failure (AMF)/change-over switch, lube oil make up system, batteries, remote alarm panel system, fuel oil system, fuel day tank (sized for at least 24 hours per day fuel consumption capacity), complete with labels, notices and ancillary materials and equipment as required to complete the installation as per the specification. | No. | 1
B | Installation of Item A above, including rigging into position on the plinth. | Item | 1
C | Supply, deliver, off-load, store on site as required and install a 150mm² 4C SWA cable between the generator and the main DB and also between the change-over switch and DB-G1. (Approximately 60m is underground and 40m is on cables racks and in ducts) | m | 100
D | Supply, deliver, off-load, store on site as required and install terminations for the 150mm² 4C SWA cables including glands and all other accessories required. | No. | 6
E | Supply, deliver, off-load, store on site as required and install 95mm² BCEW, including terminations, complete as required. | m | 100
F | Supply, deliver, off-load, store on site as required and install 300A MCCB's | m | 2
G | Supply, deliver, off-load, store on site as required and install complete earthing for the generator | Item | 1
H | Supply, deliver, off-load, store on site as required and install 300mm wide cable racks and ladder. | Item | 1
I | Allow for cold drilling across 2 separate walls. | Item | 1
TESTING AND COMMISSIONING
J | Test and commission the complete generator installation in the presence of the Consulting Engineer. | Item | 1
FUEL TANK FILLING AT PRACTICAL COMPLETION
K | At practical completion, fill the fuel day tank full of fuel (diesel), to be handed over to the client with the commissioned generator installation. | Item | 1
MAINTENANCE
L | Provide free maintenance for twelve (12No.) months, comprising preventive maintenance visits on a monthly basis plus breakdown maintenance as necessary. Preventive maintenance to be in line with an agreed schedule of checks. | Item | 1
M | Operating and Maintenance Manuals. | Item | 1
N | Provision of Client Training and Instruction. | Item | 1
O | Any additional items that the Tenderer may wish to detail: (Attach a separate list if space is not enough)
...……………………………………………………………………....
...……………………………………………………………………....
...……………………………………………………………………….
...……………………………………………………………………….
...……………………………………………………………………….
...……………………………………………………………………….
TOTAL CARRIED TO SUMMARY

## Summary
PROPOSED GENERATOR SETS FOR GIYANI
CERTIFICATE SUMMARY
Schedule |  |  | Amount | Corrected Budget Amount
1 | Preliminaries & Generals | R |  | 0
2 | Generator Plinths | R |  | #REF!
3 | Generator Installation | R
Sub Total 1 |  | R |  | #REF!
Contingencies @ 15% |  | R
Sub Total 2
VAT |  | R |  | 0
0
TOTAL |  | R