## Schedule 1-P&G's
SARS - PROPOSED GENERATOR SETS FOR HATFIELD GARDENS
SCHEDULE 1 : PRELIMINARIES AND GENERAL
| Payment |  |  |  | Rate | Amount
Item | Reference | Description | Unit | Qty | (R) | (R)
1. | SABS | SCHEDULE 1: PRELIMINARY & GENERAL
1200 A
1.1 | 8.3 | FIXED-CHARGE ITEMS
1.1.1 | 8.3.1 | Contractual Requirements | Sum | 1
1.2 | 8.3.2 | Establish Facilities on Site
1.2.1 | 8.3.2.1 | Facilities for the Contractor
1.1.3 |  | a Offices and storage sheds | Sum | 1
1.1.3 |  | b. Ablution and latrine facilities | Sum | 1
1.1.3 |  | c. Tools and Equipment | Sum | 1
1.1.3 |  | d. Water supplies, electric power & communication | Sum | 1
|  | e. Plant | Sum | 1
|  | f. Security of works | Sum | 1
1.3 | 8.3.4 | Remove Contractor's site establishment on completion | Sum | 1
1.4 | 8.4.0 | OPERATION AND MAINTENANCE OF FACILITIES
ON SITE
1.4.1 |  | Facilities for the Contractor
|  | a) Office and storage sheds | Sum | 1
|  | b) Ablution and latrine facilities | Sum | 1
|  | c) Provision of water, power and communication facilities | Sum | 1
|  | d) Tools and equipment | Sum | 1
1.5 | 8.5 | TEMPORARY WORKS
1.5.1 | 8.5.1 | a) Protection of infrastructure until completion of project | Sum | 1
1.5.2 | 8.5.2 | Existing Services
|  | b) Excavate by hand in soft material to expose all underground services | Sum | 1
1.6 | 8.6 | OCCUPATIONAL HEALTH AND SAFETY
1.6.1 |  | Risk Assessment Procedure, QM, Quality Management System, Health and Safety Specification, Environmental Plan, Safety Inspections, OHSA Appointments, Non-Conformance Process to be available in office [Payment after certification by SARS Clerk of Works (CoW) that above documentation is in place, according to SARS requirements and implemented] | Sum | 1
1.7 |  | Any additional items that the Tenderer may wish to detail: (Attach a separate list if space is not enough)
1.7.1 |  | ...……………………………………………………………
1.7.2 |  | ...………………………………………………………………
TOTAL CARRIED TO SUMMARY

## Schedule 2, Civil & Mecha Works
SARS - PROPOSED GENERATOR SETS FOR HATFIELD GARDENS
SCHEDULE 2: CIVIL AND MECHANICAL WORKS
| Payment |  |  |  | Rate | Amount
Item | Reference | Description | Unit | Qty | (R) | (R)
2.3.0 |  | PALISADE FENCE AND GATES
2.3.1 |  | Steelwork
|  | a) Supply and fix a high security 1.8m high, hot dip galvanised invisible fence with minimum 3.00mm thickness on horizontal and vertical strands. Apertures to be approximately 76 x 12mm. Fence to be power tool resistant and difficult to climb. Fence must have a minimum of a 25 year guarantee for normal conditions. Rate to include all posts, excavations, concrete and fittings for complete fence. CONTRACTOR TO TAKE SPECIAL NOTE OF THE PARTICULAR SPECIFICATION DOCUMENT. | m | 9.5
|  | b) Extra over for Suppy and fit of 76x51x4.8 L Double angle Cleat connection bolted onto existing walls and welded onto Invisible fence post | Sum | 4
|  | c) Supply and install 1800m wide swing steel gate to match palisade fence. Complete with hinges connections etc | Sum | 1
2.4 |  | Other Extras
|  | New cylinder locksets for gate | No | 1
2.5 |  | MECHANICAL WORKS
|  | a) Fire Department Approval for installation and usage of Generator | Sum | 1
|  | b) Supply and Install SANS approved 9kg D.C.P (Dry Powder) fire extinguisher | No | 1
|  | c) Supply and install SANS approved 5kg aluminium CO2 (Carbon Dioxide) fire extinguisher | No | 1
Total carried Forward
Total brought Down
2.6 |  | SIGNAGE
|  | a) SABS approved signage for Fire extinguishers and all required statutory signs for the generator area (e.g. No smoking, no access etc) | Sum | 1
2.7 |  | Final commisioning of the works including removal of rubble, dust and and other waste generated during construction. | Sum | 1
2.8 |  | Any additional items that the Tenderer may wish to detail: (Attach a separate list if space is not enough)
2.8.1 |  | ...……………………………………………………………
2.8.2 |  | ...……………………………………………………………
2.8.3 |  | ...……………………………………………………………
TOTAL CARRIED TO SUMMARY

## Schedule 3, Electrical
SARS - PROPOSED GENERATOR SETS FOR HATFIELD GARDENS
SCHEDULE 3: ELECTRICAL WORKS - GENERATOR INSTALLATION
Item | Description | Unit | Qty | Rate ( R ) | Amount ( R )
STANDBY GENERATOR INSTALLATION
3.1 | SCHEDULE 3: GENERATOR INSTALLATION
3.1.1 | Supply, deliver to site, off-load and store on site as required a prime rated 150 kVA diesel generator set as specified, scheduled and shown on the drawings, including all materials, exhaust system (with approximately 05 metre exhaust pipe), automatic mains failure (AMF)/change-over switch, lube oil make up system, batteries, remote alarm panel system, fuel oil system, full fuel day tank (sized for at least 24 hours per day fuel consumption capacity), complete with labels, notices and ancillary materials and equipment as required to complete the installation as per the specification. | No. | 1
3.1.2 | LV Cable Excavation and Re-compactment | m | 90
3.1.3 | Supply, deliver, off-load, store on site as required and install a 95mm² 4C SWA cable between the generator and the main DB. It is also between the change-over switch and DB-Ground floor and First floor. Refer to the attached Tender Drawing. (Approximately 90m of cable is underground and 80m is on cables racks and in ducts) | m | 170
3.1.4 |  | m | 170
3.1.5 | Supply, deliver, off-load, store on site as required and install terminations kit for the 95mm² 4C SWA cables including glands and all other accessories required. | No. | 6
3.1.6 | Supply, deliver, off-load, store on site as required and install 50mm² BCEW, including terminations kit, complete as required. | m | 150
3.1.7 | Supply, deliver, off-load, store on site as required and install 250A MCCB's Triple Pole | No. | 2
3.1.8 | Supply, deliver, off-load, store on site as required and install 200A MCCB's Triple Pole | No. | 1
3.1.9 | Supply, deliver, off-load, store on site as required and install complete earthing for the generator | Sum | 1
3.1.10 | Supply, deliver, off-load, store on site as required and install 200mm wide cable racks and ladder. With the insuclusion of necessary components and bends | Sum | 1
3.1.11 | Allowance for cold drilling across 4 separate walls | Sum | 1
3.1.12 | Galvanised Steel Cable Tray | m | 60
3.2 | TESTING AND COMMISSIONING
3.2.1 | Test and commission the complete generator installation in the presence of the Consulting Engineer. | Sum | 1
3.3 | FUEL TANK FILLING AT PRACTICAL COMPLETION
3.3.1 | At practical completion, fill the fuel day tank full of fuel (diesel), to be handed over to the client with the commissioned generator installation. | Sum | 1
3.4 | MAINTENANCE
3.4.1 | Provide free maintenance for twelve (12) months, comprising preventive maintenance visits on a monthly basis plus breakdown maintenance as necessary. Preventive maintenance to be in line with an agreed schedule of checks. | Sum | 1
3.4.2 | Operating and Maintenance Manuals. | Sum | 1
3.4.3 | Provision for Client Training and Instruction. | Sum | 1
3.5 | Any additional items that the Tenderer may wish to detail: (Attach a separate list if space is not enough)
3.5.1 | ...…………………………………………………………………
3.5.2 | ...…………………………………………………………………
3.5.3 | ...……………………………………………………………………
3.5.4 | ...…………………………………………………………………
3.5.5 | ...……………………………………………………………………
TOTAL CARRIED TO SUMMARY

## Summary
PROPOSED GENERATOR SETS FOR HATFIELD GARDENS
SUMMARY OF WORKS
Item | Description |  | Amount | Corrected Budget Amount
1 | Schedule 01 - Preliminaries & Generals | R |  | 0
2 | Schedule 02 - Civil and Mechanical Works | R |  | #REF!
3 | Schedule 03 - Electrical Works: Generator Installation | R
4 | Sub Total 1 | R |  | #REF!
5 | Contingencies @ 15% | R
6 | Sub Total 2 | R
7 | VAT@14% | R |  | 0
0
8 | GRAND TOTAL | R