## P&G's
FIRE PROTECTION INSTALLATION BILLS OF QUANTITIES
Project Name : LAHAE LA SARS - BLOCK E |  |  |  | Date: | 2022-08-15
Drawing Reference : 21B09-F-505-01 |  |  |  | Page: | 1 of 5
Location : BROOKLYN |  |  |  | Prepared by: | T.E
Floor level : GROUND STOREY |  |  |  | Revision: | 1
BILL N°1 PRELIMINARY AND GENERAL ITEMS
Item N° | Description | Unit | Qty. | Rate | Amount R c
Bidders shall allow for all the clauses as referred to in the "Agreement and Schedule of Principal Building Agreement" as issued by the Joint Building Contracts Committee.
ALL ITEMS SHALL BE PRICED INDIVIDUALLY AS A LUMP SUM WILL NOT BE ACCEPTABLE!
Tenderer shall allow for whatever cost he may consider necessary for Preliminary and General Items to carry out the Mechanical Installations in full, as detailed in the drawings, Specifications and Schedules, which shall include, but shall not be limited,
1.1 | Testing & Commissioning of installation | Item | 1
1.2 | Clearing | Item | 1
1.3 | Site meetings | Item | 1
1.4 | Installation - shop drawings | Item | 1
1.5 | Submission of electrical requirements for Mechanical equipment and installation | Item | 1
1.6 | Labelling of equipment | Item | 1
1.7 | Operation and maintenance manuals- 3 -off paper and 3-off pdf electronic copies on CD | Item | 1
1.8 | Provision of As built Drawings and documents | Item | 1
1.9 | Any necessary calculations requested by the engineer | Item | 1
1.10 | Equipment submissions | Item | 1
1.11 | Statutory authorities - site inspections | Item | 1
1.12 | Training and Hand over of installation to client | Item | 1
1.13 | Any other items (Specify) | Item | 1
Total for this page carried forward to next page: |  |  |  |  | -
`

## BILL 2 - BLOCK E
FIRE PROTECTION INSTALLATION BILLS OF QUANTITIES
Project Name : LAHAE LA SARS - BLOCK E |  |  |  | Date: | 2022-08-15
Drawing Reference : 21B09-F-505-01 |  |  |  | Page: | 2 of 5
Location : BROOKLYN |  |  |  | Prepared by: | T.E
Floor level : GROUND STOREY |  |  |  | Revision: | 1
BILL N°2 FIRE PROTECTION SYSTEM
Section 1. HAND HELD FIRE PROTECTION EQUIPMENT (FIRE EXTINGUISHERS) Refer to drawings: 21B09-F-505-01
Item N° | Description | Unit | Qty. | Rate | Amount R c
1 | FIRE EXTINGUISHERS INSTALLATION: Supply, delivery, installation, connection, testing and commissioning of a completely functioning Fire extinguishers installation as itemised below:
1.1 | 4.5 kg DCP Fire Extinguisher | No. | 4 |  | 0
2 | EXISTING FIRE EXTINGUISHERS - Servicing of fire extinguishers itemised below:
2.1 | 4.5 kg DCP Fire Extinguisher | No. | 7 |  | 0
3 | STATUTORY EMERGENCY SIGNAGE: Supply, delivery, installation, cleaning and commissioning of statutory emergency signage installation in accordance with this document and SANS 1186 Parts 1 and 5 – including all anodised aluminium frames, hooks, chains and other fixing materials as required. Note all signage must 190mm high, Photoluminescent, with a visible SABS stamp of approval, and must be mechanically screw fixed.
3.1 | Running man & arrow sign - E1 | No. | 5 |  | 0
3.2 | Running man & arrow sign - E2 | No. | 6 |  | 0
3.3 | Running man, arrow pointing down - E3 | No. | 5 |  | 0
3.4 | Arrow and extinguisher sign - F13 | No. | 3 |  | 0
3.5 | Arrow and extinguisher sign - F16 | No. | 3 |  | 0
3.6 | Arrow and extinguisher sign - F19 | No. | 3 |  | 0
3.7 | Arrow, extnguisher, hose reel, hydrant sign - F1 | No. | 1 |  | 0
3.8 | Arrow, extnguisher, hose reel, hydrant sign - F2 | No. | 1 |  | 0
3.9 | Arrow, extnguisher, hose reel, hydrant sign - F3 | No. | 1 |  | 0
3.10 | Arrow, extinguisher, hose reel sign - F4 | No. | 3 |  | 0
3.11 | Arrow, extinguisher, hose reel sign - F5 | No. | 3 |  | 0
3.12 | Arrow, extinguisher, hose reel sign - F6 | No. | 3 |  | 0
3.13 | Break Glass unit - F31 | No. | 2 |  | 0
3.14 | Fire exit keep clear - F45 | No. | 2 |  | 0
3.15 | Exit sign - E6 | No. | 2 |  | 0
4 | FIRE RATED DOORS: Supply, delivery, of Fire doors equal and approved to Allandale, Amador, & SDA. The doors must be SABS approved, with certification tags on both the door frame and door leaf as itemised below: Note the fire doors must have steel frames with 25mm rebates as per SANS 10400 and SANS 1253
4.1 | 60 minute fire rated doors - 1200mm (wide) x 2100mm (high), Single door, single swing complete with door closer. | No. | 5 |  | 0
5 | FIRE SEALING: Supply, and Installation of SABS approved 60 minute Fire sealing elements with certification reports as itemised below:
5.1 | Supply and install 60min fire rated fire sealing elements to gap between top of separation wall (between fire zones & Underside of slab/roof). | m | 103.086 |  | 0
5.2 | Supply and install fire sealing for Shaft floor penetration & wall - fire water pipe, electrical cables, data cables,etc | Item | 2 |  | 0
6 | Any other items (Specify) | Item | Sum
Total for Bill No.2 carried forward to the final collection page: |  |  |  |  | 0

## BILL 3 - EQUIPMENT & PIPING
FIRE PROTECTION INSTALLATION BILLS OF QUANTITIES
Project Name : LAHAE LA SARS - BLOCK E |  |  |  | Date: | 2022-07-20
Drawing Reference : 21B09-F-505-01 |  |  |  | Page: | 3 of 5
Location : BROOKLYN |  |  |  | Prepared by: | T.E
Floor level : GROUND STOREY |  |  |  | Revision: | 1
BILL N°3 FIRE PROTECTION SYSTEM
Section 1. HAND HELD FIRE PROTECTION EQUIPMENT (FIRE HYDRANTS, FIRE HOSE REELS & PIPING) Refer to drawings: 21B09-F-505-01
Item N° | Description | Unit | Qty. | Rate | Amount R c
1 | HOSE REEL HYDRANTS AND EXTINGUISHER INSTALLATION Supply, delivery, installation, connection, testing and commissioning of a completely functioning hose reel installation as itemised below:
1.1 | Supply & Install Fire Hose Reels (30m long), complete with chromium plated 25mm valve fittings (not plastic), with pressure gauges, hose roller guides and service stickers (on the drum and face of the hose reel) with all required fixings. | No. | 1 |  | 0
2 | FIRE HYDRANT INSTALLATION Supply, delivery, installation, connection, testing and commissioning of a completely functioning fire hydrant installation as itemised below:
2.1 | 100mm diameter wall mounted type high efficiency fire hydrant fully installed at site | No. | 1 |  | 0
2.2 | 100mm diameter Class 16 HDPE connecting main from booster connection to external hydrant positions including breaking in, elbows, fittings, hangers, offsets around structure, thrust blocks, trenching and backfilling. | m | - |  | By Civils
3 | HOSE REEL PIPING SUPPLY & INSTALLATION Supply, delivery, installation, connection, testing and commissioning of a completely functioning hose reel installation as itemised below:
3.1 | Supply & Install of Black Steel c/w fittings and supports for above ground installation as specified
3.1.1 | 100mm Nominal Bore | m | 3.45 |  | -
3.1.2 | 25mm Nominal Bore | m | 23.1644 |  | 0
3.1.3 | Painting and identification of all fire pipe work as per SABS | Item | Sum |  | 0
3.1.4 | Pipework Flushing as per SABS | Item | Sum |  | 0
3.1.5 | Pipework Pressure Test as per SABS | Item | Sum |  | 0
4 | EXISTING HOSE REEL SERVICING Servicing of fire hose reel | No. | 2
5 | Any other items (specify) | Item | Sum
Total for Bill No.5 carried forward to the final collection page: |  |  |  |  | 0

## BILL 4 - Builder Work
FIRE PROTECTION INSTALLATION BILLS OF QUANTITIES
Project Name : LAHAE LA SARS - BLOCK E |  |  |  | Date: | 2022-08-15
Drawing Reference : 21B09-F-505-01 |  |  |  | Page: | 4 of 5
Location : BROOKLYN |  |  |  | Prepared by: | T.E
Floor level : GROUND STOREY |  |  |  | Revision: | 1
BILL N°4 BUILDERS WORK
Refer to drawings: 21B09-F-505-01
Item N° | Description | Unit | Qty. | Rate | Amount R c
1 | Wall penetration for fire water supply pipes
1.1 | Wall penetration for fire water supply pipe | No. | 2
2 | Door fittings & others
2.1 | Supply & Install panic bar doors single leaf escape | No. | -
2.2 | Supply & Install panic bar doors double leaf escape | No. | -
2.3 | Supply & Install Door closers | No. | 6
3 | New Fire Door Installation indicating the following:
3.1 | Fit/Install door frame & screw to structure | No. | 6
3.2 | Fill the door cavity top & 2-sides | No. | 6
3.3 | Hang door leaf & plane if needed to complete with painting / sealing planed sides | No. | 6
3.4 | Mount Fire Rating tags on door frames & leaf | No. | 12
3.5 | Paint walls & make good | No. | 6
4 | Install Fire extinguisher backing boards timber painted red fixed to wall 400(H) x 150(W) x 25mm thick as supplied by fire contractor | No. | 4
5 | Any other items (specify) | Item | Sum
`
Total for bill No.6 carried forward to the final collection page:

## Final Collection Page
FIRE PROTECTION INSTALLATION BILLS OF QUANTITIES
Project Name : LAHAE LA SARS - BLOCK E |  |  |  | Date: | 2022-08-15
Drawing Reference : 21B09-F-505-01 |  |  |  | Page: | 5 of 5
Location : BROOKLYN |  |  |  | Prepared by: | T.E
Floor level : GROUND STOREY |  |  |  | Revision: | 1
FINAL COLLECTION PAGE
Item N° | Description |  | Amount R c
1 | Bill No. 1 Preliminary and General |  | -
2 | Bill No. 2 - BLOCK E - Ground Storey - Fire Protection Extinguishers, Fire Separation Elements & Signage |  | 0
3 | Bill No. 3 - Hand Held Fire Protection Equipment and Piping Fire Hose Reel, Hydrants and Piping |  | 0
4 | Bill No. 4 - Builder's Work Wall Penetrations
#VALUE!
5 | Subtotal (Items 1 to 6) |  | 0
6 | Provisional sum allowance At the discretion of the Engineer for the supply and installation of the systems |  | 50000
6.1 | Additional fire signage which may be required by fire department | 5000
6.2 | Construction changes | 8000
6.3 | Additional fire equipment | 7000
6.4 | Additional fire sealing | 10000
6.5 | Fire water pressure and flow test | 20000
7 | Subtotal (Items 7 to 8)
8 | Add VAT (15% of The item 9)
9 | Total Contract Value (Items 9 and 10)
Total Contract Value Carried to Main Contractor's Bill |  |  | 0
`