## boq
SARS WAREHOUSE CAPE TOWN
Mechanical hvac installation: boq
Item no. | Description | Unit | Quantity | Rate | Amount
Refer to Technical Specifaction:
2190315-Mechanical hvac Specification
Refer to Dwgs:
2190315-HVAC-02
2190315-HVAC-03
2190315-HVAC-04
1 | Section 1
1.1 | Item 6: Provide all scaffolding, lifting and plant equipment needed for the durantion of the contract | item
1.2 | Item 12: Provide all drawings as specified | item
1.3 | Item 13: Provide operation and maintenance manuals as specified | item
1.4 | Item 14: Provide maintenance and guarantee as specified | item
1.5 | Item 20: Commissioning as specified and required | item
1.6 | Item 21: Training as specified | item
Total general technical items carried forward to summary
Section 2:
2 | FAF-S-01 fan system
2.1 | Weather cowl, galvanised sheet metal flanged with bird mesh screen | no | 1
2.2 | Filter, 495x395x50 WP77 washable pleated complete with housing, frame, clips and side sliding access | no | 1
2.3 | Attenuator, inlet side, flanged, 850 long, complete with galvanised steel mounting brackets | no | 1
2.4 | Attenuator, outlet side, flanged, 1,100 long, complete with galvanised steel mounting brackets | no | 1
2.5 | Fan, FAF-S-01 complete with mounting brackets flanged and hard connected to attenuators | no | 1
2.6 | Flexible connection, connecting outlet attenuator to transformation piece | no | 1
2.7 | Transformation piece, galvanised sheet metal - attenuator size to 300x300 | no | 1
2.8 | Transformatioin piece, galvanised sheet metal ducting, 250x200 to 200x200 | no | 1
2.9 | Bend, galvanised sheet metal, 300x300 | no | 2
2.10 | Bend, galvanised sheet metal, 200x200 | no | 7
2.11 | Bend, galvanised sheet metal, 250x200 | no | 1
2.12 | Ducting, galvanised sheet metal, 300x300 | m | 4
2.13 | Ducting, galvanised sheet metal ducting, 200x200 | m | 35
2.14 | Ducting, galvanised sheet metal, 250x200 | m | 11
2.15 | Ducting, galvanised sheet metal circular ducting, Ø125 | m | 3
2.16 | Reducer, galvanised ducting, 250x200 to 200x200 | no | 1
2.17 | Flexible ducting, Ø125 | m | 3
2.18 | Saddle, galvanised sheet metal, 200x200 connected to 300x300 ducting | no | 1
2.19 | Saddle, galvanised sheet metal, 250x200 connected to 300x300 ducting | no | 1
2.20 | Saddle, galvanised sheet metal, 200x200 connected to 250x200 ducting | no | 2
2.21 | Fire damper, with sleeve, 300x300 | no | 1
2.22 | Fire damper, with sleeve, 250x200 | no | 1
2.23 | Fire damper, with sleeve, 200x200 | no | 3
2.24 | Double deflection supply air grille, SAG-1 complete with shoe connection piece and obd | no | 8
2.25 | Double deflection supply air grille, SAG-2 complete with shoe connection piece and obd | no | 2
2.26 | Disc valve, SAV-1 complete with 1m Ø125 flexible connection | no | 2
2.27 | Door grilles, DG-1, complete | no | 5
Electrical installation
2.28 | Isolator, weather proof, within 1m of fan | no | 1
2.29 | Conduit, galvanised Ø25 complete with saddles | m | 2
2.30 | Electrical wiring, isolator to fan | m | 2.5
2.31 | Timer, electronic 7-day timer suitable for switchboard mounting | no | 1
Total for FAF-S-01 fan system carried forward to summary
3 | FAF-S-02 fan system
3.1 | Weather louvre, WL-2 galvanised steel with bird mesh screen, 800x400 | no | 1
3.2 | Filter, 625x392x50 WP77 washable pleated complete with housing, frame, clips and side sliding access | no | 1
3.3 | Attenuator, inlet side, flanged, 850 long, complete with galvanised steel mounting brackets | no | 1
3.4 | Attenuator, outlet side, flanged, 850 long, complete with galvanised steel mounting brackets | no | 1
3.5 | Fan, FAF-S-02 complete with mounting brackets flanged and hard connected to attenuators | no | 1
3.6 | Flexible connection, connecting fan & attenuator combination to ducting, both sides | no | 2
3.7 | Transformation piece, galvanised sheet metal, 800x400 to attenuator size | no | 1
3.8 | Transformatioin piece, galvanised sheet metal, attenuator size to 400x300 | no | 1
3.9 | Ducting, galvanised sheet metal, 400x300 | m | 5
3.10 | Fire damper, FD-02 complete with screen on both sides of damper, including galvanised steel wall sleeve, 400x400 | no | 2
3.11 | Double deflection supply air grille, SAG-1, 350x250 complete with shoe connection piece and obd | no | 4
Electrical installation
3.12 | Isolator, weather proof, within 1m of fan | no | 1
3.13 | Conduit, galvanised Ø25 complete with saddles | m | 2
3.14 | Electrical wiring, isolator to fan | m | 2.5
3.15 | Isolator within 1m of FD-02 | no | 2
3.16 | Conduit, galvanised Ø25 complete with saddles - isolator to FD-02 | m | 2
3.17 | Electrical wiring, isolator to FD-02 | m | 5
Total for FAF-S-02 fan system carried forward to summary
4 | EAF-EX-01 fan system
4.1 | Weather louvre, WL-1 galvanised steel with bird mesh screen, 400x400, complete with galvanised steel wall sleeve | no | 1
4.2 | Weather louvre, WL-2 galvanised steel with bird mesh screen, 800x400, complete with galvanised steel wall sleeve and flanged connection for fire damper | no | 1
4.3 | Fan, EAF-EX-01 complete with mounting brackets | no | 1
4.4 | Transformation piece, galvanised sheet metal, Fan discharge to 400x400 weather louvre | no | 1
4.5 | Balancing Damper, 400x400 | no | 1
4.6 | Fire damper, FD-01, 800x400, complete with screen on inside, flanged, with motorised drive to class II | no | 1
Electrical installation (class II)
4.7 | Isolator, within 1m of equipment (fan and FD-01) | no | 2
4.8 | Conduit, galvanised Ø25 complete with saddles | m | 4
4.9 | Electrical wiring, isolator to equipment | m | 5
Total for EAF-EX-01 fan system carried forward to summary
5 | EAF-EX-02 fan system
5.1 | Weather louvre, WL-1 galvanised steel with bird mesh screen, 400x400, complete with galvanised steel wall sleeve | no | 1
5.2 | Fan, EAF-EX-02 complete with mounting brackets | no | 1
5.3 | Transformation piece, galvanised sheet metal, Fan discharge to 400x400 weather louvre | no | 1
5.4 | Balancing Damper, 400x400 | no | 1
Electrical installation (class II)
5.5 | Isolator, within 1m of equipment | no | 1
5.6 | Conduit, galvanised Ø25 complete with saddles | m | 2
5.7 | Electrical wiring, isolator to equipment | m | 2.5
Total for EAF-EX-02 fan system carried forward to summary
6 | EAF-EX-03 fan system
6.1 | Weather louvre, WL-1 galvanised steel with bird mesh screen, 400x400, complete with galvanised steel wall sleeve | no | 1
6.2 | Weather louvre, WL-2 galvanised steel with bird mesh screen, 800x400, complete with steel wall sleeve and flanged connection for fire damper | no | 1
6.3 | Fan, EAF-EX-03 complete with mounting brackets | no | 1
6.4 | Transformation piece, galvanised sheet metal, Fan discharge to 400x400 weather louvre | no | 1
6.5 | Fire damper, FD-01, 800x400, complete with screen on inside, flanged, with motorised drive to class I | no | 1
6.6 | Balancing Damper, 400x400 | no | 1
Electrical installation (Class I)
6.7 | Isolator, within 1m of equipment (fan and FD-01) | no | 2
6.8 | Conduit, galvanised Ø25 complete with saddles | m | 4
6.9 | Electrical wiring, isolator to equipment | m | 5
Total for EAF-EX-03 fan system carried forward to summary
7 | EAF-EX-04 fan system
7.1 | Weather louvre, WL-1 galvanised steel with bird mesh screen, 400x400, complete with steel wall sleeve | no | 1
7.2 | Fan, EAF-EX-04 complete with mounting brackets | no | 1
7.3 | Transformation piece, galvanised sheet metal, Fan discharge to 400x400 weather louvre | no | 1
7.4 | Balancing Damper, 400x400 | no | 1
Electrical installation (Class I)
7.4 | Isolator, within 1m of equipment | no | 1
7.5 | Conduit, galvanised Ø25 complete with saddles | m | 2
7.6 | Electrical wiring, isolator to equipment | m | 2.5
Total for EAF-EX-04 fan system carried forward to summary
8 | SAF-S-01 Smoke extract fans
8.1 | Removal of entire existing smoke extract system (6 fan installations) and hand over to client | no | 1
8.2 | Weather louvre, galvanised steel with bird mesh screen, complete with galvanised steel wall sleeve | no | 1
8.3 | Fan, SAF-S-01 complete with mounting brackets | no | 1
8.4 | Transformation piece, steel, fan discharge to weather louvre sleeve | no | 1
8.5 | Bellmouth inlet, steel with inlet screen | no | 1
Electrical installation
8.6 | Isolator, within 1m of equipment | no | 1
8.7 | Conduit, galvanised Ø25 complete with saddles | m | 2
8.8 | Electrical wiring, isolator to equipment | m | 2.5
Total for SAF-S-01 smoke extract fan carried forward to summary
9 | SAF-S-02/03/04/05/06/07/08 Smoke extract fans
9.1 | Weather louvre, galvanised steel with bird mesh screen, complete with steel sleeve sealed against window frames | no | 7
9.2 | Fan, SAF-S-02/03/04/05/06/07/08 complete with mounting brackets | no | 7
9.3 | Transformation piece, steel, fan discharge to weather louvre sleeve | no | 7
9.4 | Bellmouth inlet, steel with inlet screen | no | 7
9.5 | Fire/smoke curtain as specified. Item complete | Item | 1
Electrical installation
9.6 | Isolator, within 1m of equipment | no | 1
9.7 | Conduit, galvanised Ø25 complete with saddles | m | 2
9.8 | Electrical wiring, isolator to equipment | m | 2.5
Total for SAF-S-02/03/04/05/06/07/08 smoke extract fan carried forward to summary
Section 4:
Electrical installation
10 | DB-01
10.1 | DB-01, Smoke Fans DB/Control Panel, complete as specified with making off supply power cable and fire detection signal | no | 1
10.2 | Cable trays, 200 wide, galvanised, wall mounted with all bends, T-junctions, from DB to fan isolators | m | 100
10.3 | Power supply cables to smoke extract fans, neatly tied to cable ladder, connected to DB on one side and isolator on other side | m | 314
10.4 | Protecting power distribution cables from DB to fan isolators and fan with in-tumescent paint | no | 1
10.5 | Power cables to fire / smoke curtain, complete with cable trays and isolator/s | item | 1
10.6 | Remote control panel for smoke fans; complete with wiring and cable trays | item | 1
Total for electrical installation, DB-01 Smoke Fans DB/Control Panel carried forward to summary
11 | DB-02
11.1 | DB-02, Fan DB/ Control Panel, complete as specified with making off supply power cable and fire detection signal | no | 1
11.2 | Cable trays, 200 wide, galvanised, wall mounted with all bends, T-junctions, from DB to outside wall (running below slab) in hazardous material lobby | m | 35
11.3 | Power supply cables to EAF-EX-01/02/03/04; FAF-S-02; FD-02 (two off); FD-01 (two off), neatly tied to cable ladder, connected to DB on one side and isolators on other side, all to the specified insulation class | m | 210
11.4 | Protecting power distribution cables from DB to equipment isolators with in-tumescent paint | no | 1
Total for electrical installation, DB-02 Fans DB/Control Panel carried forward to summary

## Summary
SARS WAREHOUSE CAPE TOWN
Mechanical hvac installation: Summary boq
Item no. | Description | Unit | Quantity | Rate | Amount
1 | Total general technical items carried over from boq
2 | Total for FAF-S-01 fan system carried over from boq
3 | Total for FAF-S-02 fan system carried over from boq
4 | Total for EAF-EX-01 fan system carried over from boq
5 | Total for EAF-EX-02 fan system carried over from boq
6 | Total for EAF-EX-03 fan system carried over from boq
7 | Total for EAF-EX-04 fan system carried over from boq
8 | Total for SAF-S-01 smoke extract fan carried over from boq
9 | Total for SAF-S-02/03/04/05/06/07/08 smoke extract fan carried over from boq
10 | Total for electrical installation DB-01 Smoke Fans DB/Control Panel carried over from boq
11 | Total for electrical installation DB-02 Fans DB/Control Panel carried over from boq
Total for mechanical hvac installation carried forward to main boq