## Bill No.1
BILL NO1: FIRE PROTECTION INSTALLATION
Item | Description | Unit | Quantity | Tarif | Amount
All in accordance with the drawings and specification
SPRINKLER SYSTEM
Price given below shall be nett cost of equipment and materials supplied and installed on site and shall:
a) | Include profit, overheads, financing, insurance and guarantee costs
b) | Include engineering and management costs
c) | Exclude VAT
Sprinkler installation control valve including all valve trim fittings and equipment such as alarm gong, flow switch and gauges.
1 | Ø200 (Sprinklers with Bypass arrangement) | No | 1 |  | 0
2 | Ø200 mm Valve Manifold with 1 x Ø150 Control Valve & 1 x Ø100 Control Valve outlets. | No | 1 |  | 0
3 | Flow proving arrangement | No | 1 |  | 0
Fire pump room and valve room protection
4 | Ø 50 Flow switch | No | 1 |  | 0
5 | Ø 50 Gate Valve | No | 1 |  | 0
6 | Sprinkler protection to valve room (No of Heads) | No | 1 |  | 0
7 | Sprinkler protection to pump room (No of Heads) | No | 4 |  | 0
All Sprinkler mains complete supply & installation from ICV up to and including remote area of operation for each sprinkler array, excluding pump room supply and floor piping but including all piping, hangers fittings and supports and air relief valves (Purge Valves) & Pressure relief valves
8 | Ø 150 Mains | m | 275 |  | 0
9 | Ø 100 Mains | m | 200 |  | 0
10 | Ø 100 to canopies | m | 30 |  | 0
Sprinkler Pump mains installation from pump house to manifold
11 | Ø200 Steel pipe 4.5mm wall | m | 6 |  | 0
12 | Fire pump room piping: All piping from the water tanks to the fire pump delivery header including all valves, fittings for new pump sets. | Item | 1 |  | 0
13 | Direct reading flow meter | No. | 1 |  | 0
14 | Remote test valve, including valve, sight glass and 15 mm orifice, all fittings and equipment complete as shown on the tender drawings. | No | 10 |  | 0
In-Fill Supply to tanks
15 | Ø 100 Supply Mains | m | 150 |  | 0
16 | Ø 100 Underground Supply Mains u-pvc Class 16 | m | 45 |  | 0
17 | Ø100 Tank In-Fill including shut off valve, strainer check valve and flow control valve to new tank. | Item | 1 |  | 0
18 | Trenching, Bedding & backfilling for tank infill piping. | m | 45 |  | 0
19 | In-fill tank direct reading flow measuring apparratus. | Item | 1 |  | 0
All Sprinklers K 8.0 Including all Ranges complete supply & installation including, hangers, fittings, painting and supports and air relief valves (Purge Valves)
Floor Piping installation, including Range piping, all fittings, hangers, supports, brackets, bracing, Trapeze bars,couplings and sprinkler heads complete per zone as follows (Based on cost per sprinkler head)
20 | Valve 1: Sprinklers to Roof - 141°C K8.0 (metric) Pendant Spray | No | 679 |  | 0
21 | Sprinklers to Offices - 68°C K8.0 (metric) Pendant Conventional | No | 25 |  | 0
22 | Sprinklers to Canopies - 68°C K8.0 (metric) Upright Conventional | No | 50 |  | 0
23 | Valve 2: In-rack Sprinklers - 141°C K11.5 (metric) Pendant Spray | No | 686 |  | 0
24 | Water Storage tank (GVTec Stainless Steel tanks) including all suction lines, valves, peripherals, fittings and accessories as specified, (2 x 250 m³ Tank capacity). ASIB approved and tested | No | 1 |  | 0
25 | Diesel driven fire pump and day tank complete with all fittings and accessories as specified, starting arrangement etc To curve in specification. ASIB approved and tested | No | 1 |  | 0
26 | Diesel driven fire pump controller and annunciator panel complete with all fittings and accessories as specified. ASIB approved and tested | No | 1 |  | 0
27 | Jockey pump and controller complete with all fittings and accessories as required. ASIB approved and tested | No | 1 |  | 0
28 | Operating and maintenance manuals and as built drawings | Item | 1 |  | 0
29 | Plant room and valve room framed and laminated instruction block plans and schematics. | Item | 1 |  | 0
Spare parts as listed below:
30 | Diesel pump manufacturers spares recommended | Sets | 1 |  | 0
31 | Diesel Engine manufacturers spares recommended | Sets | 1 |  | 0
32 | Valve Gaskets and seals (1 per valve) | Sets | 1 |  | 0
33 | Pressure switches | No | 1 |  | 0
34 | Flow switches | No | 1 |  | 0
35 | Standard K 8.0 141°C Sprinklers (Spray) | No | 12 |  | 0
36 | Standard K 8.0 68°C Sprinklers (Conventional) | No | 6 |  | 0
37 | Standard K 11.5 141°C Sprinklers (Spray) | No | 12 |  | 0
38 | Sprinkler Wrench | No | 2 |  | 0
39 | Recommended other spares etc (List and detail)
40 | Training of staff | Item | 1 |  | 0
41 | Any item not listed (Specify)
0
0
0
TOTAL TRANSFERRED TO "SUMMARY OF TENDER BILLS" - ITEM 1 |  |  |  |  | 0

## Bill No.2
BILL NO2: FIRE WATER INSTALLATION
Item | Description | Unit | Quantity | Tarif | Amount
All in accordance with the drawings and specification
FIRE HYDRANT & FIRE HOSE REEL SYSTEM
Price given below shall be nett cost of equipment and materials supplied and installed on site and shall:
a) | Includeprofit, overheads, financing, insurance and guarantee costs
b) | Include engineering and management costs
c) | Exclude VAT
Fire piping: Allow for connecting to the existing fire mains.
1 | Ø 100 Isolating Valve | No | 1 |  | 0
Fire Hose reel main piping in warehouse: including all fittings, hangers, supports, brackets, bracing, couplings and droppers to outlets
2 | Ø 100 galvanized Steel | m | 150 |  | 0
3 | Ø 65 galvanized Steel | m | 70 |  | 0
4 | Ø 32 galvanized Steel | m | 10 |  | 0
5 | Ø 25 galvanized Steel droppers | m | 75 |  | 0
6 | Fire hydrants complete: Fire hydrant complete with brackets, unions and line pressure guage with proper vent cock. | No | 11 |  | 0
7 | Fire hose reel complete: Fire hose reel complete with mounting brackets, and mounting stands, valve and union and line pressure guage with proper vent cock. | No | 5 |  | 0
Fire extinguishers complete with backing boards and holding clips
8 | - 4.5 kg DCP | No | 2 |  | 0
9 | - 9 kg DCP | No | 48 |  | 0
10 | - 5kg CO2 | No | 2 |  | 0
TOTAL TRANSFERRED TO "SUMMARY OF TENDER BILLS" - ITEM 2 |  |  |  |  | 0

## Bill No.3
BILL NO3: SCAFFOLDING AND ERECTION EQUIPMENT, PAINTING & REMOVAL OF OLD SPRINKLER SYSTEM.
Item | Description | Unit | Quantity | Tarif | Amount
1 | SCAFFOLDING Allow for the provision, erection, use, dismantling and transportation of scaffolding in accordance with the requirements of the Occupational Health and Safety Act (Act 85 of 1993). | Item | 1 |  | 0
2 | ERECTION EQUIPMENT Allow for any additional erection equipment required for the installation of the system to all portions of the building as indicated on the tender drawings. | Item | 1 |  | 0
3 | Allow for the existing system to be removed in its entirety. | Item | 1 |  | 0
4 | Allow for 1 x shop coat of etch primer and 2 x coats of signal red enamel to all pipework. | Item | 1 |  | 0
TOTAL TRANSFERRED TO "SUMMARY OF TENDER BILLS" - ITEM 3 |  |  |  |  | 0

## Bill No.4
BILL NO 4: SUMMARY OF TENDER BILLS
ITEM | BILL | AMOUNT
DESCRIPTION
1 | BILL NO 1 : SPRINKLER SYSTEM | 0
2 | BILL NO 2 : FIRE WATER SYSTEM | 0
3 | BILL NO 3 : SCAFFOLDING AND ERECTION EQUIPMENT | 0
TOTAL TENDER VALUE - FIRE PROTECTION INSTALLATION |  | 0