## Bill A
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
A | PREAMBLES TO BILLS OF QUANTITIES
A1 | These Bills of Quantities contain pages numbered
consecutively.
A2 | Before the Tenderer submits his tender he should check
the number of pages, and if any are found missing or
duplicated, or the figures or writing indistinct, he should
apply to the Engineer at once and have same rectified as
no liability whatsoever will be admitted by the Engineer in
respect of errors in tender due to the foregoing.
A3 | The Bills of Quantities form part of and must be read in
conjunction with the Specification, which document
contains the full description of the work to be done and
material and equipment to be used and unless otherwise
described in the Bills of Quantities, reference should be
made to the Specification for the full meaning of
descriptions of work to be done and materials and
equipment to be used in this service.
A4 | All item rates and extensions must be priced in detail
before submission of Tenders..
A5 | The total tender price in the bill shall constitute the contract
price of the successful Tenderer.
A6 | Tenderers are advised to check their item extensions and
total additions, as no claim for arithmetical arrors will be
considered.
A7 | No alteration, erasure or addition is to be made in the text
of the Bills of Quantities. Should any alteration, erasure or
addition be made, it will not be recognised but the original
wording of the Bills of Quantities will be adhered to.
A8 | The priced Bills of Quantities of the successful Tenderer
will be checked and the Engineer reserves the right to call
for adjustments to any individual price and to rectify any
discrepancy whilst the Total Tender Price, as submitted,
remains unaltered.
A9 | The responsibility for the accuracy of the quantities written
into the Bills remains with the person who prepared the
Bills. The Tenderer shall be relieved of responsibility of
measuring quantities at the tender stage, and the tender
sum submitted shall be in respect of the quantities set out
in the Bills, although he will be required to make his
assessment of items such as copper fittings, etc.,
from details stated in the Bills and specification.
CARRIED FORWARD

## Bill A1
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
TOTAL CARRIED FORWARD
A10 | The quantities in these Bills of Quantities are provisional
and are not to be used for ordering materials.
A11 | Variations in the scope and extent of the work
included in the Bills shall be allowed to meet
the Employer's requirements and shall be measured
and costed at rates entered in the Bills.
`
Any items or variation for which rates have not been
included in the Bills shall be agreed and priced as
non-scheduled items in accordance with the provisions of
the contract.
A13 | The description of each item shall, unless otherwise stated
herein, be held to include making, conveying and
delivery, profit and all other obligations arising out of
the Conditions of Contract.
A14 | All measurements are nett, unless otherwise stated, and
Tenderers must allow in the rate for wastage.
A16 | All materials or equipment specified under a trade name,
catalogue or reference number shall, for competitive
tender pricing, be exactly as described in this tender.
CARRIED TO SUMMARY SHEET

## VRF Air Conditioning
SUPPLY ONLY OF VRF AIR CONDITIONING SYSTEMS
SIXTH FLOOR
SECTION : MECHANICAL BILL OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
The following bill of quantities must be read in conjunction with the foregoing specifications as well as the attached mechanical engineer's drawings No M01.JNB.000014/AC/01 Tenderer's attention is specifically drawn to the guarantee against defects, servicing and maintenance period and the testing and commissioning clauses, which is applicable to the whole of the air conditioning and ventilation installation. The contractor has to allow for these costs in his/her unit rates.
All equipment as measured shall be deemed to be complete as described in the specifications and include fixing on mounting brackets if so required, connection to water supplies, waste and or overflow pipe work, etc.
Electrical work shall be carried out in accordance with SANS 10142 code of practice as described.
Anti-vibration mountings, supports, hangers, brackets and accessories are to be used where required to the satisfaction of the engineer.
Rates are to include for condensate drainage piping from evaporator unit to drains including any necessary PVC sleeves through walls and condensate pumps.
Although shortened descriptions had been used in this bill, tenderers must carefully read the specifications to acquaint themselves with the full description and specifications of the equipment.
Whichever brand is proposed by the tenderer, no additional charges shall be entertained for any integrator equipment etc that may be necessary to communicate with a central controller system that supports all installations on site to be installed under a different contract. The majority of these installations are either Midea or Midea compatible products (Infinity range). The tenderer shall be required to enter additional costs that shall be attributable to this requirement against this item and should no costs be entered it shall be deemed that there are no additional costs associated with this item.
| TOTAL CARRIED FORWARD |  |  |  | 0
| TOTAL BROUGHT FORWARD |  |  |  | 0
1. | Variable Refrigerant Volume System Installation
Supply and install heat recovery type outdoor condensing unit complete with mounting ancillaries, refrigerant charge, electrical connection and wiring between outdoor unit and indoor unit complete as specified and as per drawing. All necessary distributor fittings and MS boxes etc are deemed to be included here.
1.1.1 | 6th Flr System Outdoor units - minimum required cooling capacity of 97.6 kW | No | 1
1.1.3 | Condenser coil treatment - BLUCHEM or other approved for outdoor condensers as per above |  | SUM
1.2 | Supply and install indoor units complete with mounting ancillaries, refrigerant charge, electrical connection, filters on return air side, complete as specified and as per drawing. These units are to include for condensate drain pumps
1.2.1 | AC – 6/1 - Ducted Hide-away - Total Cooling Required – 8 kW | No | 1
1.2.2 | AC – 6/2 - Ducted Hide-away - Total Cooling Required – 8 kW | No | 1
1.2.3 | AC – 6/3 - Ducted Hide-away - Total Cooling Required – 11.2 kW | No | 1
1.2.4 | AC – 6/4 - Compact Cassette - Total Cooling Required – 4.5 kW | No | 1
1.2.5 | AC – 6/5 - Compact Cassette - Total Cooling Required – 4.5 kW | No | 1
1.2.6 | AC – 6/6 - Compact Cassette - Total Cooling Required – 2.2 kW | No | 1
1.2.7 | AC – 6/7 - Compact Cassette - Total Cooling Required – 4.5 kW | No | 1
1.2.8 | AC – 6/8 - Compact Cassette - Total Cooling Required – 4.5 kW | No | 1
1.2.9 | AC – 6/9 - Ducted Hide-away - Total Cooling Required – 20 kW | No | 1
| TOTAL CARRIED FORWARD |  |  |  | 0
| TOTAL BROUGHT FORWARD |  |  |  | 0
1.2.10 | AC – 6/10 - Compact Cassette - Total Cooling Required – 7.2 kW | No | 1
1.2.11 | AC – 6/11 - Ducted Hide-away - Total Cooling Required – 14 kW | No | 1
1.2.12 | AC – 6/12 - Compact Cassette - Total Cooling Required – 4.5 kW | No | 1
1.2.13 | AC – 6/13 - Ducted Hide-away - Total Cooling Required – 9 kW | No | 1
1.3 | Wall mounted Controllers
1.3.1 | Wall mounted fixed type controllers | No | 13
1.4 | System Controller
1.4.1 | System Controller as specified |  | Sum
1.5 | Insulated Condensate drainage pipes, the contractor is required to price for the full drainage installation |  | Sum
1.6 | Supply and install VRF refrigerant piping complete with mounting brackets, cable trays, insulation, all as specified and as per drawing.
1.6.1 | 6.4 mm diameter copper refrigerant pipe | m | 21
1.6.2 | 9.5 mm diameter copper refrigerant pipe | m | 24
1.6.3 | 12,7 mm diameter copper refrigerant pipe | m | 29
1.6.4 | 15.9 mm diameter copper refrigerant pipe | m | 20
1.6.5 | 19.1 mm diameter copper refrigerant pipe | m | 14
1.6.6 | 22.2 mm diameter copper refrigerant pipe | m | 14
1.6.7 | 28.6 mm diameter copper refrigerant pipe | m | 9
1.6.8 | 31.8 mm diameter copper refrigerant pipe | m | 3
1.7 | Extra over for fittings (90 degree bends, tee's etc)
1.7.1 | Contractor to indicate quantity
1.7.2 | 6.4 mm diameter copper | No
1.7.3 | 9.5 mm diameter copper | No
| TOTAL CARRIED FORWARD |  |  |  | 0
| TOTAL BROUGHT FORWARD |  |  |  | 0
1.7.4 | 12,7 mm diameter copper | No
1.7.5 | 15.9 mm diameter copper | No
1.7.6 | 19.1 mm diameter copper | No
1.7.7 | 22.2 mm diameter copper | No
1.7.8 | 25.4 mm diameter copper | No
1.7.9 | 22.2 mm diameter copper | No
1.7.10 | 25.4 mm diameter copper | No
1.7.11 | 28.6 mm diameter copper | No
1.7.12 | 31.8 mm diameter copper | No
2 | DUCTING (As per SANS 1238.)
Flexible duct connection between ducted hide-away unit and sound attenuator and return air plenum and unit, size to suit unit offered.
2.1 | Supply air | No | 5
2.2 | Return air | No | 5
Supply and install galvanised mild steel ducting, including hangers, supports, jointing, sealing, 25 mm FRK external liner insulation, fixing materials as specified and as per drawings - metal thickness as per SANS 1238
2.3 | Transformation pieces
2.3.1 | SDA F4 to 1450 x 150 (750 long) | No | 6
2.4 | Straight pieces
2.4.1 | 350 mm diameter | m | 5
2.4.2 | 300 mm diameter | m | 5
2.4.3 | 250 mm diameter | m | 5
2.4.4 | 200 mm diameter | m | 5
2.4.5 | 150 mm diameter | m | 5
| TOTAL CARRIED FORWARD |  |  |  | 0
| TOTAL BROUGHT FORWARD |  |  |  | 0
2.5 | 90° Bends
2.5.1 | 300 mm diameter | No | 5
2.5.2 | 250 mm diameter | No | 5
2.5.3 | 200 mm diameter | No | 5
2.5.4 | 150 mm diameter | No | 5
2.6 | Spigots
2.6.1 | 300 mm diameter | No | 5
2.6.2 | 250 mm diameter | No | 5
2.6.3 | 200 mm diameter | No | 5
2.6.4 | 150 mm diameter | No | 5
2.7 | Insulated Flexible Duct
Supply and install insulated flexible ducting, including hangers, supports, jointing, sealing, fixing materials as specified and as per drawing - thickness as per SABS 10173
2.7.1 | 300 mm diameter | m | 5
2.7.2 | 250 mm diameter | m | 5
2.7.3 | 200 mm diameter | m | 5
2.7.4 | 150 mm diameter | m | 5
2.8 | Sound Attenuators
Supply and install sound attenuators Donkin PGL Series or equal as specified and as shown on the drawings:
2.8.1 | SDA-F4: 850 x 1375 x 500 | No | 6
3 | SITE LOCATION AND ATTENDANCE
3.1 | Delivery, transport, attendance to site and other costs associated with the logistics involved |  | Sum
| TOTAL CARRIED FORWARD |  |  |  | 0
| TOTAL BROUGHT FORWARD |  |  |  | 0
4 | OCCUPATIONAL HEALTH AND SAFETY
4.1 | Compliance with OHS Act and Construction Regulation 2003 as well as the Health and Safety Specification |  | Sum
4.2 | Health and Safety Plan to be complied by a reputable external OHS Act consultant for the use of this contract |  | Sum
5 | STRIPPING AND REMOVAL OF EXISTING SERVICES
5.1 | Stripping of existing VRF system and all redundant associated piping, cabling etc |  | Sum
5.2 | Removal of all equipment not required harvesting of plant for spares |  | Sum
6 | TESTING AND COMMISSIONING
6.1 | Commissioning of entire Sixth Floor air conditioning installation |  | Sum
6.2 | Three sets of operating and maintenance manuals |  | Sum
6.3 | As Built Drawings |  | Sum
7 | CONTRACTUAL MAINTENANCE
7.1 | Daily site cleaning during construction |  | Sum
7.2 | Three minor services (1 every 3 months) |  | Sum
7.3 | One major service (final service) |  | Sum
8 | SUNDRIES
8.1 | Workshop drawings and equipment schedule submittals for approval prior to ordering |  | Sum
8.2 | Training of staff |  | Sum
9 | ADDITIONAL ITEMS
Items not listed in the bill which the Contractor might deem necessary in order to complete the installation in working order. Rates only.
| TOTAL CARRIED FORWARD |  |  |  | 0
| TOTAL BROUGHT FORWARD |  |  |  | 0
Should the Contractor not list items below it will be assumed that he is satisfied with the contents of the Bill where upon no claim for unlisted items will be entertained during or at the conclusion of the contract.
| TOTAL CARRIED TO SUMMARY PAGE |  |  |  | 0

## Bill Summary
SUPPLY AND INSTALLATION OF VRF AIR CONDITIONING SYSTEMS
SIXTH FLOOR
SECTION : SUMMARY OF MECHANICAL BILLS OF QUANTITIES
| 1 | SUPPLY AND INSTALLATION OF VRF AIR CONDITIONING SYSTEMS | 0
| 2 | P&G's | R
| 3 | SUB-TOTAL | #VALUE!
| 4 | ADD MARK-UP | #VALUE!
| 5 | TOTAL FOR PROJECT TO BE CARRIED OVER TO FINAL SUMMARY – VOLUME ONE | #VALUE!
CONTRACTORS NAME:-
ADDRESS:- ----------------------------------------------------------------------------------
---------------------------------------------------------------------------------
CONTACT DETAILS:-
TELEPHONE:- -------------------------------------------------------------------------------
FAX:- -------------------------------------------------------------------------------
SIGNATURE:- -----------------------------------------------------------