ELECTRICAL SPECIFICATION FOR

SARS OFFICES: LE HAE LA SARS, PRETORIA

ELECTRICAL REFUBISHMENT

GENERAL SPECIFICATION FOR ELECTRICAL WORK: PART 1

Index

PART 1 -  GENERAL	1

C.1 CONDUIT AND CONDUIT ACCESSORIES	8

1.	GENERAL	8

2.	SCREWED CONDUIT	8

3.	METAL CONDUIT ACCESSORIES	8

4.	CIRCULAR TYPE BOXES	8

5.	SWITCH BOXES AND SOCKET OUTLET BOXES	8

6.	FLEXIBLE CONDUIT	9

7.	EARTH CLAMPS	9

C.2 WIRING CHANNELS, UNDERFLOOR DUCTING AND POWER SKIRTING	10

1.	WIRING CHANNELS	10

2.	UNDERFLOOR DUCTING	11

3.	POWER SKIRTING	11

c.3  CABLE TRAYS AND LADDERS	12

1.	METAL CABLE TRAYS	12

2.	CABLE LADDERS	12

3.	PLASTIC CABLE TRAYS	12

4	FINISHES	12

5.	ACCESSORIES	13

C.4  PVC-INSULATED CABLES   600/1 000 V GRADE	14

1.	GENERAL	14

2.	CONSTRUCTION	14

3.	PVC-SHEATHED ALUMINIUM-COVERED CABLES	14

4.	LENGTHS	14

5.	TESTS	14

C.5  GLANDS FOR PVC-INSULATED CABLES	15

C.10  LIGHT SWITCHES	16

1.	GENERAL	16

2	FLUSH AND SURFACE MOUNTED SWITCHES	16

3.	WATERTIGHT SWITCHES	16

4.    	CEILING SWITCHES	16

5.   	COVER PLATES	16

C.11  UNSWITCHED AND SWITCHED SOCKET-OUTLETS	17

1.	GENERAL	17

2.	FLUSH AND SURFACE MOUNTED SWITCHED SOCKETS	17

3.   	WATERTIGHT SWITCHED SOCKETS	17

4.   	UNSWITCHED SOCKET-OUTLETS	17

5.  	THREE-PHASE SWITCHED SOCKET-OUTLETS	17

6.    	SHAVER SOCKETS	18

C.12  LUMINAIRES FOR INTERIOR AND EXTERIOR APPLICATIONS	19

C.12.1  TUBULAR FLUORESCENT LAMP LUMINAIRES FOR INTERIOR APPLICATIONS	19

1.   	SCOPE	19

2.   	GENERAL	19

3.    	STANDARDS	19

4.	PHYSICAL AND ENVIRONMENTAL REQUIREMENTS	19

5.   	GENERAL TECHNICAL REQUIREMENTS	20

6.   	PHOTOMETRIC DATA	21

7.   	TECHNICAL INFORMATION	21

8.   	CHANNEL LUMINAIRE	21

9.    	INDUSTRIAL LUMINAIRES	22

10.	DECORATIVE LUMINAIRES	22

11.   	RECESSED LUMINAIRES	22

12.   	LOW-BRIGHTNESS LUMINAIRES	22

13.   	LOW GLARE LUMINAIRES	22

14.	LUMINAIRES FOR USE IN AREAS WITH VISUAL DISPLAY TERMINALS	23

C12.3  BULKHEAD LUMINAIRES FOR USE WITH COMPACT FLUORESCENT OR TUNGSTEN FILAMENT LAMPS FOR INTERIOR AND EXTERIOR APPLICATIONS	24

1.   	SCOPE	24

2.   	GENERAL	24

3.    	STANDARDS	24

4.   	PHYSICAL AND ENVIRONMENTAL REQUIREMENTS	24

5.	GENERAL TECHNICAL REQUIREMENTS	25

6.   	PHOTOMETRIC DATA	26

7.    	TECHNICAL INFORMATION	26

C.15  BUSBARS (RISING AND OVERHEAD FOR VOLTAGES UP TO 1 kV)	27

1.	GENERAL	27

2.   	BUSBAR ENCLOSURE	27

3.	PAINT FINISH	27

4.   	BUSBARS	27

5.   	EARTHING OF METAL PARTS	30

6.   	BOLTS AND NUTS	30

7.   	ACCESSORIES AND CONNECTIONS	30

8.   	FUSED TAKE-OFFS	30

9.   	FIRE BARRIERS	30

10. 	TESTING	30

C.16  EARTHING ELECTRODES	33

1.	GENERAL	33

2.	CATEGORY AND TYPE	33

3.   	COUPLINGS AND CONDUCTOR CLAMPS	33

C.17  SWITCHBOARDS (Up to 1 kV)	34

1.	GENERAL	34

2.   	CONSTRUCTION OF FLUSH MOUNTED SWITCHBOARDS	34

3.   	CONSTRUCTION OF SURFACE MOUNTED SWITCHBOARDS	35

4.   	CONSTRUCTION OF FREE STANDING SWITCH BOARDS	35

5.   	CONSTRUCTION OF MAIN LOW TENSION SWITCHBOARDS	38

6.  	MOUNTING OF EQUIPMENT	38

7. 	BUSBARS IN SWITCHBOARDS	40

8.    	WIRING	40

10.  	LABELLING	43

11 	TESTS	44

12.	DRAWINGS	44

C.20  MOULDED-CASE CIRCUIT-BREAKERS	46

C.24  EARTH LEAKAGE RELAYS	47

C.30  TIME SWITCHES AND PHOTOCELLS	48

1.    	GENERAL	48

2.	CONSTRUCTION	48

3.    	OPERATING CONDITIONS	48

4.    	TECHNICAL REQUIREMENTS	48

C.31  CONTACTORS	49

C.33  INDOOR SURGE ARRESTORS	51

C.34  WORKMANSHIP OF STAFF AND CERTIFICATE OF COMPLIANCE	52

SECTION C1

# PART 1 -  GENERAL

- 1	TESTS

- After completion of the works and before first delivery is taken, a full test will be carried out on the installation for a period of sufficient duration to determine the satisfactory working thereof.  During this period the installations will be inspected and the Contractor shall make good, to the satisfaction of the Representative/Agent, any defects which may arise.

- The Contractor shall provide all instruments and equipment required for testing and any water, power and fuel required for the commissioning and testing of the installations at completion.

- 2	MAINTENANCE OF INSTALLATIONS

With effect from the date of the First Delivery Certificate the Contractor shall at his own expense undertake the regular servicing of the installation during the maintenance period and shall make all adjustments necessary for the correct operation thereof.

If during the said period the installations is not in working order for any reason for which the Contractor is responsible, or if the installations develops defects, he shall immediately upon being notified thereof take steps to remedy the defects and make any necessary adjustments.

Should such stoppages however be so frequent as to become troublesome, or should the installations otherwise prove unsatisfactory during the said period the Contractor shall, if called upon by the Representative/Agent, at his own expense replace the whole of the installations or such parts thereof as the Representative/Agent may deem necessary with apparatus specified by the Representative/Agent.

- 3	REGULATIONS

The installation shall be erected and tested in accordance with the Acts and Regulations as indicated in the scope of works

- 4	NOTICES AND FEES

- The Contractor shall give all notices required by and pay all necessary fees, including any inspection fees, which may be due to the local Supply Authority.

- On production of the official account, only the net amount of the fee charged by the Supply Authority for connection of the installation to the supply mains, will be refunded to the Contractor by SARS.

- 5	SCHEDULE OF FITTINGS

- In all instances where schedule of light, socket outlet and power points are attached to or included on the drawings, these schedules are to be regarded as forming part of the specification.

- 6	QUALITY OF MATERIALS

- Only materials of first class quality shall be used and all materials shall be subject to the approval of SARS.  Departmental specifications for various materials to be used on this Contract are attached to and form part of this specification.

- Wherever applicable the material is to comply with the relevant South African Bureau of Standards, specifications, or to British Standard Specifications, where no SABS Specifications exist.

- Materials wherever possible, must be of South African manufacture.

- 7	CONDUIT AND ACCESSORIES

The type of conduit and accessories required for the service, i.e. whether the conduit and accessories shall be of the screwed type, plain-end type or of the non-metallic type and whether metallic conduit shall be black enamelled or galvanised, is specified in Part 2  of this specification.

Unless other methods of installation are specified for certain circuits, the installation shall be in conduit throughout.  No open wiring in roof spaces or elsewhere will be permitted.

The conduit and conduit accessories shall comply fully with the applicable SABS specifications as set out below and the conduit shall bear the mark of approval of the South African Bureau of Standards.

- Screwed metallic conduit and accessories:  SABS 1065, parts 1 and   2.

- Plain-end metallic conduit and accessories:  SABS 1065, parts 1 and 2.

- Non-metallic conduit and accessories:  SABS 950

All conduit fittings except couplings, shall be of the inspection type.  Where cast metal conduit accessories are used, these shall be of malleable iron.  Zinc base fittings will not be allowed.

Bushes used for metallic conduit shall be brass and shall be provided in addition to locknuts at all points where the conduit terminates at switchboards, switch-boxes, draw-boxes, etc.

Draw-boxes are to be provided in accordance with the “Wiring Code” and wherever necessary to facilitate easy wiring.

For light and socket outlet circuits, the conduit used shall have an external diameter of 20mm.  In all other instances the sizes of conduit shall be in accordance with the “Wiring Code”  for the specified number and size of conductors, unless otherwise directed in part 2 of this specification or indicated on the drawings.

Only one manufactured type of conduit and conduit accessories will be permitted throughout the installation.

Running joints in screwed conduit are to be avoided as far as possible and all conduit systems shall be set or bent to the required angles.  The use of normal bends must be kept to a minimum with exception of larger diameter conduits where the use of such bends is essential.

All metallic conduit shall be manufactured of mild steel with a minimum thickness of 1,2mm for plain-end conduit and 1,6mm in respect of screwed conduit.

Under no circumstances will conduit having a wall thickness of less than 1,6mm be allowed in screeding laid on top of concrete slabs.

Bending and setting of conduit must be done with special bending apparatus manufactured for the purpose and which are obtainable from the manufacturers of the conduit systems.  Damage to conduit resulting from the use of incorrect bending apparatus or methods applied must on indication by SARS’s inspectorate staff, be completely removed and rectified and any wiring already drawn into such damaged conduits must be completely renewed at the Contractor’s expense.

Conduit and conduit accessories used for flame-proof or explosion proof installations and for the suspension of luminaires as well as all load bearing conduit shall in all instances be of the metallic screwed type.

All conduit and accessories used in areas within 50 km of the coast shall be galvanised to SABS 763.

Tenderers must ensure that general approval of the proposed conduit system to be used is obtained from the local electricity supply authority prior to the submission of their tender.  Under no circumstances will consideration be given by SARS to any claim submitted by the Contractor, which may result from a lack of knowledge in regard to the supply authority’s requirements.

- 8	CONDUIT IN ROOF SPACES

- Conduit in roof spaces shall be installed parallel or at right angles to the roof members and shall be secured at intervals not exceeding 1,5m by means of saddles screwed to the roof timbers.

- Nail or crampets will not be allowed.

- Where non-metallic conduit has been specified for a particular service, the conduit shall be supported and fixed with saddles with a maximum spacing of 450 mm.  The Contractor shall supply and install all additional supporting timbers in the roof space as required.

- Under flat roofs, in false ceilings or where there is less than 0,9m of clearance, or should the ceilings be insulated with glass wool or other insulating material, the conduit shall be installed in such a manner as to allow for all wiring to be executed from below the ceilings.

- Conduit runs from distribution boards shall, where possible terminate in fabricated sheet steel draw-boxes installed directly above or in close proximity to the boards.

- 9	SURFACE   MOUNTED CONDUIT

- Wherever possible, the conduit installation is to be concealed in the building work; however, where unavoidable or otherwise specified under Part 2 of the specification, conduit installed on the surface must be plumbed or levelled and only straight lengths shall be used.

- The use of inspection bends is to be avoided and instead the conduit shall be set uniformly and inspection coupling used where necessary.

- No threads will be permitted to show when the conduit installation is complete, except where running couplings have been employed.

- Running couplings are only to be used where unavoidable, and shall be fitted with a sliced couplings as a lock nut.

- Conduit is to be run on approved spaced saddles rigidly secured to the walls.

- Alternatively, fittings, tees, boxes, couplings etc., are to be cut into the surface to allow the conduit to fit flush against the surface.  Conduit is to be bedded into any wall irregularities to avoid gaps between the surface and the conduit.

- Crossing of conduits is to be avoided, however, should it be necessary purpose-made metal boxes are to be provided at the junction.  The finish of the boxes and positioning shall be in keeping with  the general layout.

- Where several conduits are installed side by side, they shall be evenly spaced and grouped under one purpose-made saddle.

- Distribution boards, draw-boxes, industrial switches and socket outlets etc., shall be neatly recessed into the surface to avoid double sets.

- In situations where there are no ceilings the conduits are to be run along the wall plates and the beams.

- Painting of surface conduit shall match the colour of the adjacent wall finishes.

- Only approved plugging materials such as aluminium inserts, fibre plugs, plastic plugs, etc., and round-head screws shall be used for fixing saddles, switches, socket outlets, etc., to walls, wood plugs and the plugging in joints in brick walls are not acceptable.

- 10	CONDUIT IN CONCRETE SLABS

- In order not to delay building operations the Contractor must ensure that all conduits and other electrical equipment which are to be cast in the concrete columns and slabs are installed in good time.

- The Contractor shall have a representative in attendance at all times when the casting of concrete takes place.

- Draw-boxes, expansion joint boxes and round conduit boxes are to be provided where necessary.  Sharp bends of any nature will not be allowed in concrete slabs.

- Draw and/or inspection boxes shall be grouped under one common cover plate, and must preferable be installed in passages or male toilets.

- All boxes, etc., are to be securely fixed to the shuttering to prevent displacement when concrete is cast.  The conduit shall be supported and secured at regular intervals and installed as close as possible to the neutral axis of concrete slabs and/or beams.

- Before any concrete slabs are cast, all conduit droppers to switchboards shall be neatly spaced and rigidly fixed.

- 11	FLEXIBLE  CONNECTIONS  FOR  CONNECTING  UP  OF  STOVES,  MACHINES,  ETC.

- Flexible tubing connections shall be of galvanised steel construction, and in damp situations of the plastic sheathed galvanised steel type.  Other types may only be used subject to the prior approval of SARS’s site electrical representative.

- Connectors for coupling onto the flexible tubing shall be of the gland or screw-in types, manufactured of either brass or cadmium or zinc plated mild steel, and the connectors after having been fixed onto the tubing, shall be durable and mechanically sound.

- Aluminium and zinc alloy connectors will not be acceptable.

- 12	WIRING:

- Except where otherwise specified in Part 2 of this specification, wiring shall be carried out in conduit throughout.  Only one circuit per conduit will be permitted.

- No wiring shall be drawn into conduit until the conduit installation has been completed and all conduit ends provided with bushes.  All conduits to be clear of moisture and debris before wiring is commenced.

- Unless otherwise specified in Part 2 of this specification or indicated on the service drawings, the wiring of the installation shall be carried out in accordance with the “Wiring Code”.  Further to the requirements concerning the installation of earth conductors to certain light points as set out in the “Wiring Code”, it is a specific requirement of this document that where plain-end metallic conduit or non-metallic conduit has been used, earth conductors must be provided and drawn into the conduit with the main conductors to all points, including all luminaires and switches throughout the installation.

- Wiring for lighting circuits is to be carried out with 1,5mm² conductors and a 1,5mm²-earth conductor.  For socket outlet circuits the wiring shall comprise 4mm² conductors and a 2,5mm²-earth conductor.  In certain instances, as will be directed in Part 2 of this specification, the sizes of the aforementioned conductors may be increased for specified circuits.  Sizes of conductors to be drawn into conduit  in all other instances, such as feeders to distribution boards, power points etc., shall be as specified elsewhere  in this specification or indicated on the drawings.  Sizes of conductors not specified must be determined in accordance with the “Wiring Code”.

- The loop-in system shall be followed throughout, and no joints of any description will be permitted.

- The wiring shall be done in PVC insulated 600/1000 V grade cable to SABS 150.

- Where cable ends connect onto switches, luminaires etc., the end strands must be neatly and tightly twisted together and firmly secured.  Cutting away of wire strands of any cable will not be allowed.

- 13	SWITCHES AND SOCKET OUTLETS

- All switches and switch-socket outlet combination units shall conform to SARS Quality Specifications, which form part of this specification.

- No other than 16 A 3 pin sockets are to be used, unless other special purpose types are distinctly specified or shown on the drawings.

- All light switches shall be installed at 1,4m above finished floor level and all socket outlets as directed in the Schedule of Fittings which forms part of this specification or alternatively the height of socket outlets may be indicated on the drawings.

- 14	SWITCHGEAR

- Switchgear, which includes circuit breakers, iron-clad switches, interlocked switch-socket outlet units, contactors, time switches, etc., is to be in accordance with SARSal Quality Specifications which form part of this specification and shall be equal and similar in quality to such brands as may be specified.

- For uniform appearance of switchboards, only one approved make of each of the different classes of switchgear mentioned in the Quality Specifications shall be used throughout the installations.

- 15	SWITCHBOARDS

- All boards shall be in accordance with the types as specified, be constructed according to the detail or type drawings and must be approved by SARS before installation.

- In all instances where provision is to be made on boards for the supply authority’s main switch and/or metering equipment the contractor must ensure that all requirements of the authorities concerned in this respect are met.

- Any construction or standard type aboard proposed, as an alternative to that specified must have the prior approval of SARS.

- All busbars, wiring, terminals, etc., are to be adequately insulated and all wiring is to enter the switchgear from the back of the board.  The switchgear shall be mounted within the boards to give a flush front panel.  Cable and boxes and other ancillary equipment must be provided where required.

- Clearly engraved labels are to be mounted on or below every switch.  The working of the labels in English and Afrikaans, is to be according to the lay-out drawings or as directed by SARS’s representative and must be confirmed on site.  Flush mounted boards to be installed with the top of the board 2,0m above the finished floor level.

- 16	WORKMANSHIP AND STAFF

- Except in the case of electrical installations supplied by a single-phase electricity supply at the point of supply, an accredited person shall exercise general control over all electrical installation work being carried out.

- The workmanship shall be of the highest grade and to the satisfaction of SARS.

- All inferior work shall, on indication by SARS’s inspecting officers, immediately be removed and rectified by and at the expense of the Contractor.

- 17	CERTIFICATE OF COMPLIANCE

- On completion of the service, a certificate of compliance must be issued to SARS’s Representative/Agent in terms of the Occupational Health and Safety Act, 1993  (Act 85 of 1993).

- 18	EARTHING OF INSTALLATION

- Main earthing

- The type of main earthing must be as required by the supply authority if other than SARSs, and in any event as directed by SARS’s representative, who may require additional earthing to meet test standards.

- Where required an earth mat shall be provided, the minimum size, unless otherwise specified, being 1,0m  x  1,0m and consisting of 4mm diameter hard-drawn bare copper wires at 250mm centres, brazed at all intersections.

- Alternatively or additionally earth rods or trench earths may be required as specified or directed by SARS’s authorised representative.

- Installations shall be effectively earthed in accordance with the “Wiring Code” and to the requirements of the supply authority.  All earth conductors shall be stranded copper with or without green PVC installation.

- Connection from the main earth bar on the main board must be made to the cold water main, the incoming service earth conductor, if any and the earth mat or other local electrode by means of 12mm x 1,60 mm solid copper strapping or 16 mm² stranded (not solid) bare copper wire or such conductor as SARS’s representative may direct.  Main earth copper strapping where installed below 3m from ground level, must be run in 20 mm diameter conduit securely fixed to the walls.

- All other hot and cold water pipes shall be connected with 12mm x 0,8mm perforated for solid copper strapping (not conductors) to the nearest switchboard.  The strapping shall be fixed to the pipework with brass nuts and bolts and against walls with brass screws at 150-mm centres.  In all cases where metal water pipes, down pipes, flues, etc., are positioned within 1,6m of switchboards an earth connection consisting of copper strapping shall be installed between the pipework and the board.  In vertical building ducts accommodating both metal water pipes and electrical cables, all the pipes shall be earthed at each distribution board.

- Roofs, gutters and down pipes

- Where service connections consist of overhead conductors, all metal parts of roofs, gutters and down pipes shall be earthed.  One bare 10mm² copper conductor shall be installed over the full length of the ceiling void, fixed to the top purlin and connected to the main earth conductor and each switchboard.  The roof and gutters shall be connected at 15m intervals to this conductor by means of 12mm X 0,8mm copper strapping (not conductors) and galvanised bolts and nuts.  Self-tapping screws are not acceptable.  Where service connections consist of underground supplies, the above requirements are not applicable.

- Sub-distribution boards

- A separate earth connection shall be supplied between the earth busbar in each sub-distribution board and the earth busbar in the Main Switchboard.  These connections shall consist of a bare or insulated stranded copper conductors installed along the same routes as the supply cables or in the same conduit as the supply conductors.  Alternatively armoured cables with earth continuity conductors included in the armouring may be utilised where specified or approved.

- Sub-circuits

- The earth conductors of fall sub-circuits shall be connected to the earth busbar in the supply board in accordance with SABS 0142.

- Ring Mains

- Common earth conductors may be used where various circuits are installed in the same wire way in accordance with SABS 0142.  In such instances the sizes of earth conductors shall be equivalent to that of the largest current carrying conductor installed in the wire way, alternatively the size of the conductor shall be as directed by the Engineer.  Earth conductors for individual circuits branching from the ring main shall by connected to the common earth conductor with T-ferrules or soldered.  The common earth shall not be broken.

- Non-metallic Conduit

- Where non-metallic conduit is specified or allowed, the installation shall comply with SARS’s standard quality specification for “conduit and conduit accessories”.

- Standard copper earth conductors shall be installed in the conduits and fixed securely to all metal appliances and equipment, including metal switch boxes, socket-outlet boxes, draw-boxes, switchboards, luminaires, etc. The securing of earth conductors by means of self-threading screws will not be permitted.

- Flexible Conduit

- An earth conductor shall be installed in all non-metal flexible conduit.  This earth conductor shall not be installed externally to the flexible conduit but within the conduit with the other conductors.  The earth conductor shall be connected to the earth terminals at both ends of the circuit.

- Connection

- Under no circumstances shall any connection points, bolts, screws, etc., used for earthing be utilised for any other purpose.  It will be the responsibility of the Contractor to supply and fit earth terminals or clamps on equipment and materials that must be earthed where these are not provided.

- Unless earth conductors are connected to proper terminals, the end shall be tinned and lugged.

- 19	MOUNTING AND POSITIONING OF LUMINAIRES

The Contractor is to note that in the case of board and acoustic tile ceilings, i.e. as opposed to concrete slabs, close co-operation with the building contractor is necessary to ensure that as far as possible the luminaires are symmetrically positioned with regard to the ceiling pattern.

The layout of the luminaires as indicated on the drawings must be adhered to as far as possible and must be confirmed with SARS’s representative.

Fluorescent luminaires installed against concrete ceilings shall be screwed to the outlet boxes and in addition 2 x 6mm expansion or other approved type fixing bolts are to be provided.  The bolts are to be ¾ of the length of the luminaires apart.

Fluorescent luminaires to be mounted on board ceilings shall be secured by means of two 40mm x No. 10 round head screws and washers.  The luminaires shall also be bonded to the circuit conduit by means of locknuts and brass bushes.  The fixing screws are to be placed ¾ of the length of the fitting apart.

Earth conductors must be drawn in with the circuit wiring and connected to the earthing terminal of all fluorescent luminaires as well as other luminaires exposed to the weather in accordance with the “Wiring Code”.

Incandescent luminaires are to be screwed directly to outlet boxes in concrete slabs.  Against board ceilings the luminaires shall be secured to the brandering or joists by means of two 40mm x No. 8 round head screws.

# C.1 CONDUIT AND CONDUIT ACCESSORIES

1.	GENERAL

This section covers the requirements for conduit and conduit accessories for general installations under normal environmental conditions.

The type of conduit and accessories required for the service, i.e. whether the conduit and accessories shall be of the screwed type, plain-end type or of the non-metallic type and whether metallic conduit shall be black enamelled or galvanised, is specified in Part 2 of this specification. Unless other methods of installation are specified for certain circuits, the installation shall be in conduit throughout. No open wiring in roof spaces or elsewhere will be permitted.

The conduit and conduit accessories shall comply fully with the applicable SANS Specifications as set out below and the conduit shall bear the mark of approval of the South African National Standards.

(a)	Screwed metallic conduit and accessories: SANS 1065 parts 1 and 2.

(b)	Plain-end metallic conduit and accessories: SANS 1065 Parts 1 and 2.

(c)	Non-metallic conduit and accessories: SANS 950

Bushes used for metallic conduit shall be brass and shall be provided in addition to lock nuts at all points where the conduit terminates at switchboards, switch-boxes, draw-boxes, etc.

Only one manufacture of conduit and conduit accessories will be permitted throughout the installation.

All metallic conduits shall be manufactured of mild steel with a minimum thickness of 1,2mm for plain-end conduit and 1,6mm in respect of screwed conduit.

2.	SCREWED CONDUIT

2.1	Conduits shall comply with SANS 1065 and shall bear the SANS mark.

2.2	All conduit shall be heavy gauge, welded or solid drawn, hot-dip galvanised or black enamelled, screwed tube.

2.3	Galvanised conduit shall be hot-dipped inside and outside in accordance with SANS 32 & 121.

2.4	All conduit ends shall be reamed and threaded on both sides and delivered with a coupling at one end and a plastic cap on the other end.

3.	METAL CONDUIT ACCESSORIES

All metal conduit accessories shall be of malleable cast iron or pressed steel with brass bushes in accordance with SANS 1065. Alloy or pressure cast metal accessories or zinc base alloy fittings are not acceptable. All fittings whether galvanised or black enamelled, shall be fitted with brass screws.

4.	CIRCULAR TYPE BOXES

4.1	The boxes shall be of the long spout pattern, manufactured of malleable cast iron or pressed steel and stove enamelled jet black or galvanised as required. The two cover fixing holes shall be diametrically opposite each other, drilled and tapped at 50mm centres.

4.2	Junction, draw-in and inspection boxes shall be of adequate size and shall be supplied with heavy gauge metal cover plates.

4.3	Boxes shall comply with SANS 1065.

5.	SWITCH BOXES AND SOCKET OUTLET BOXES

5.1	All switch boxes and socket outlet boxes shall be manufactured of pressed galvanised steel of at least 1mm thickness. All boxes shall be fitted with the necessary lugs to suit standard flush mounted switches and socket outlets manufactured in accordance with SANS 1085.

5.2	Light switch boxes shall be 100 x 50 x 50mm with two 20mm knockouts on the sides, one 20mm knockout on the top, bottom, side and back.

5.3	Socket outlet boxes shall be 100 x 100 x 50mm with two 20mm knockouts each on the top, bottom, sides and back.

5.4	Switch and socket outlet cover plates shall comply with SANS 1084.

6.	FLEXIBLE CONDUIT

Flexible steel conduit and adaptors shall comply with BS 731, part 1 where applicable. Flexible conduit shall be of galvanised steel construction and in damp areas of the plastic sheathed galvanised steel type. Flexible conduit shall only be used as specified and shall then be installed in accordance with par. 5.4.4 of SANS 10142.

# 7.	EARTH CLAMPS

Earth clamps shall consist of copper strips at least 1,2mm thick and not less than 12mm wide secured with a brass bolt, nut and washer and shall be so constructed that the clamp fit firmly to the conduit without any additional packing.

SECTION C.2

# C.2 WIRING CHANNELS, UNDERFLOOR DUCTING AND POWER SKIRTING

# 1.	WIRING CHANNELS

## 1.1	GENERAL

1.1.1	The channels shall be manufactured of rolled sheet steel.

1.1.2	The minimum thickness of the sheet steel shall be:

(a)	1,6mm for ribbed channels with a maximum width of 42mm.

(b)	2,5mm for unribbed channels with a maximum width of 42mm.

(c)	1,2mm for channels with a width in excess of 42mm.

1.1.3	 The channels shall be finished as follows:

| (a) In coastal areas (under all installation conditions) | Hot-dip galvanised to SANS 32 & 121 or epoxy powder coated |
| --- | --- |
| (b) Cast in concrete | Pre-galvanised |
| (c) False ceiling voids | Pre-galvanised |
| (d) Vertical building ducts coated | Hot-dip galvanised to SANS 32 & 121 or epoxy powder |
| (e) Surface mounted in plant rooms, substations, service tunnels, basements | Epoxy powder coated or electro galvanized |
| (f) Damp areas, exposed to weather underground runs in contact with earth | Hot-dip galvanised to SANS 32 & 121 or epoxy powder coated |
| (g) Undercover industrial applications | Hot-dip galvanised to SANS 32 & 121 or epoxy powder coated |

1.1.4	The above-mentioned finishes shall apply unless specified to the contrary or approved - by SARS. Hot-dip galvanised ducts shall be co!d galvanised at all joints. sections that have been cut and at places where the galvanising has been damaged. Powder coated ducts shall likewise be touched up at joints, cuts and damaged portions using methods recommended by the manufacturer of the channels.

## 1.2	Cover Plates

1.2.1	All channels shall be supplied with cover plates.

1.2.2	Channels up to 127mm wide shall have snap-in cover plates of metal or PVC.

1.2.3 	For channels wider than 127mm only metal cover plates shall be used.

1.2.4	The finish of steel cover plates shall be the same as the finish of the channels.

## 1.3	Accessories

All accessories i.e. hangers, brackets etc. shall be purpose made and in general have the same finish as the channels.

## 1.4	Wiring Supports

Wiring supports shall be provided in order to prevent the wires falling out when cover plates are removed.

# 2.	UNDERFLOOR DUCTING

## 2.1	General

2.1.1	The dueling shall be manufactured of 2mm thick rolled sheet steel or rectangular tubing. Galvanised steel shall be used or shall be epoxy coated after manufacture.

## 2.2	Outlets

2.2.1	Outlets shall be provided on a modular basis in the dueling to accommodate pedestal or recessed socket units. Tapped holes shall be provided to fix the pedestal units to the dueling.

2.2.2	Draw boxes at junctions of perpendicular ducts shall have removable barriers for wiring and shall be provided with a heavy gauge cover plate.

## 2.3	Pedestals

2.3.1	Pedestals shall be manufactured of die-cast aluminium or pressed steel.

2.3.2	The finish of pedestals shall be epoxy powder coating of an approved colour.

# 3.	POWER SKIRTING

## 3.1	General

3.1.1	The channel and cover shall be manufactured of 1mm thick rolled sheet steel.

3 1 2	The channel and cover shall be epoxy coated after manufacture.

## 3.2	Outlets

3.2.1	Outlets pre-punched on a modular basis shall be provided to accommodate socket outlets or future socket outlets.

3.2.2	In addition to standard lengths, covers of 250mm length shall be provided for installation on building module lines.

SECTION C3

# c.3  CABLE TRAYS AND LADDERS

# 1.	METAL CABLE TRAYS

Metal cable trays shall be manufactured from perforated rolled steel. Metal trays manufactured to the following standards shall be used:

(a)	Less than 150mm wide		1,2mm minimum thickness with 12mm  minimum return

(b)	150mm to 457mm			1,2mm minimum thickness with 19mm minimum return

(c)	460mm to 610mm (Heavy duty)	2,5mm minimum thickness with 76mm return

# 2.	CABLE LADDERS

2.1	Metal cable ladders shall consist of a 76mm high side rail of 2mm minimum thickness. Cross pieces shall be spaced at maximum intervals of 250mm. Where cables of 10mm2 or smaller are installed on cable ladders, the spacing of the cross pieces shall be 125mm. Cables shall be clamped in position by means of purpose-made cable clamps that fit into the cross pieces.

2.2	Cable ladders consisting of slotted metal rails which accommodate plastic or metal cable binding bands may be used in vertical cable runs against walls, etc. These cable ladders will be considered in horizontal cable runs for small cables for communication and control wiring upon the prior approval of SARS.

2.3	Purpose made cable trays consisting of 6mm angle iron and 6 x 40mm minimum cross pieces are acceptable in industrial applications. Cross pieces shall be welded in pairs at 250mm maximum centre-to-centre intervals. The pairs shall be spaced approx. 10mm apart to allow cable clamps or metallic binding bands to affix the cables to the tray.

# 3.	PLASTIC CABLE TRAYS

Rigid un-plasticine PVC cable trays complying with the following standards may be used if specified in the Detail Technical Specification:

The up stands of trays listed in (a) and (b) shall not be perforated and the top of the up stand shall be smooth. The same cable tray type shall be used in long parallel tray runs.

# 4	FINISHES

Metal cable trays and ladders shall be finished as follows:

| (a) In coastal areas | Hot-dip galvanised to SANS 32 & 121 or epoxy powder coated |
| --- | --- |
| (b) False ceiling voids | Electro-galvanised baked enamel power coated |
| (c) Vertical building ducts | Hot-dip galvanised to SANS 32 & 121 or baked enamel epoxy powder coated |
| (d) Plant rooms, substations, service tunnels | Electro-galvanised baked enamel or basements epoxy powder coated |
| (e) Damp areas, exposed to weather | Hot-dip galvanised to SANS 32 & 121 baked enamel or epoxy powder coated |
| (f) Undercover industrial application | Hot-dip galvanised to SANS 32 & 121 or baked enamel epoxy powder coated |

The above-mentioned finishes shall apply unless specified to the contrary in the Detail Technical Specification. Hot-dip galvanised trays and ladders shall be cold galvanised at all joints, sections that have been cut and at places where the galvanising has been damaged. Powder coated or enamel painted trays and ladders shall likewise be touched up at joints, cuts and damaged portions using spray canisters recommended by the manufacturer of the trays and ladders.

# 5.	ACCESSORIES

Horizontal and vertical bends, T-junctions and cross connections shall be supplied by the Contractor. The dimensions of these connections shall correspond to the dimensions of the linear sections to which they are connected. The radius of all bends shall be 1m minimum. The inside dimensions of horizontal angles or connections shall be large enough to ensure that tine allowable bending radius of the cables is not exceeded. Sharp angles shall be 45 mitred.

SECTION C4

# C.4  PVC-INSULATED CABLES   600/1 000 V GRADE

# 1.	GENERAL

This section covers the requirements for PVC-insulated cables for general installations under normal environmental conditions.

# 2.	CONSTRUCTION

2.1	Cables shall be manufactured in accordance with SANS 1507, shall come only from fresh stocks, and shall be constructed as follows:

(a)	Unarmoured cables PVC-insulated/PVC-sheathed

(b)	Armoured cables	PVC-insulated/PVC-bedded/armoured/black extruded PVC outer sheath

(c)	Single core cables PVC-insulated/unsheathed

2.2	The conductors shall be of high conductivity annealed stranded copper and the cores may be shaped or circular.

2.3	The insulation shall be general purpose PVC, 600/1 000V Grade.

2.4	The bedding shall consist of a continuous impermeable sheath of PVC extruded to fit the core or cores closely and in the case of multi-core cables, to fill the interstices between the cores.

2.5	Where armouring is specified it shall consist of one layer of galvanised steel wire in the case of multi-core cables and nonmagnetic metallic wire in the case of single core cables. Aluminium strip or tape armouring is not acceptable.

2.6	Where specified, an earth continuity conductor shall be provided in the armouring in accordance with SANS 1507.

# 3.	PVC-SHEATHED ALUMINIUM-COVERED CABLES

3.1	Aluminium-covered cables shall comprise PVC-insulated copper conductors protected by an aluminium foil tape screen and a PVC sheath.

3.2	Cable ends shall be made off with compression glands fitted with a neoprene ring to seal the end.

3.3	Aluminium sheathed cable shall be installed on surface only using matching saddles installed at suitable intervals to prevent sagging.

  - Where exposed to sunlight, the cable shall have a stabilised black outer sheath.

# 4.	LENGTHS

Cable shall be manufactured and supplied in one length to the lengths specified unless these lengths exceed a standard drum length in which case a ruling shall be obtained from SARS.

# 5.	TESTS

At the option of SARS, acceptance tests shall be carried out on production runs of the cable in accordance with SANS 1507.

SECTION C5

# C.5  GLANDS FOR PVC-INSULATED CABLES

1.	Glands to be used for terminating PVC/PVC/SWA/PVC cables shall be of the adjustable type.

2.	Glands shall be suitable for general purpose 600/1 000 V Grade cable with steel armouring.

3.	The glands shall be made of nickel-plated cadmium plated or in coastal area bronze or brass.

4.	The glands shall consist of a barrel carrying a cone bush screwed into one end and a nickel-plated brass nipple carrying a nickel-plated brass or a heavy galvanised steel locknut screwed into the other end. The galvanising shall comply with SANS 32 & 121.

5.	Non-watertight glands must be easily converted to watertight glands by means of a waterproofing shroud and inner seal kit. On the cable entry side of the barrel a concave groove shall be provided to accommodate the top rim of the waterproofing shroud.

6.	The shrouds shall be made of non-deteriorating neoprene or other synthetic rubber, and shall be resistant to water, oil and sunlight. The shrouds shall fit tightly around the glands and cable.

7.	Glands shall be provided with ISO threads and shall be suitable for the specified cable sizes.

8.	Flameproof glands shall comply with SANS 808, Groups 1, 2a and 2b.

9.	Suitable accessories shall be provided with glands to be used on ECC armoured cables to facilitate a bolted lug connection of the earth continuity conductors. Grooves cut into the barrel or cone bush to accommodate the earth continuity conductors are not acceptable.

- For unarmoured cables the cone bush and compression ring of the gland shall be replaced with a synthetic rubber compression bush and ring to provide the required grip on the outer sheath of the cable.

SECTION C10

# C.10  LIGHT SWITCHES

# 1.	GENERAL

This section covers the requirements for switches for use in general installations under normal environmental conditions.

# 2	FLUSH AND SURFACE MOUNTED SWITCHES

2.1	All switches shall be suitable for mounting in 100 x 50 x 50mm boxes shall comply  with SANS 1663 and shall bear the SANS mark.

2.2	Switches shall be of tumbler operated microgap type rated at 16A, 220/250V.

2.3	Switches shall have protected terminals for safe wiring.

2.4	Contacts shall be of silver material.

2.5  	On multi-lever switches, it shall be possible to individually change any of its switches.

2.6   	The yoke strap shall be slotted to allow for easy alignment.

2.7   	The covers of surface mounted switches shall have toggle protectors.

2.8   	Where light switches are installed in partitions, they shall, where possible, be of the special narrow type intended for installation into the mullions.

# 3.	WATERTIGHT SWITCHES

3.1   	Watertight switches shall be of the microgap type suitable for surface mounting and shall bear the SANS mark.

3.2   	The housing shall be of galvanised cast iron or die cast aluminium with watertight cover plate and toggle.

3.3 	The switch shall have a porcelain base and a quick acting spring mechanism and shall be rated at 16A, 220/250V.

3.4  	The ON/OFF position shall be clearly marked on the switch housing.

# 4.    	CEILING SWITCHES

4.1   	Ceiling switches shall be rated at 10A. 220/250V and shall be suitable for ceiling mounting on a round conduit box.

4.2   	The switch shall be made of high impact strength nylon material.

4.3   	Adequate space shall be provided within the unit for ease of wiring.

  - The switch colour shall be white and shall be fitted with a nylon cord 1.25m long.

# 5.   	COVER PLATES

5.1		Cover plates shall be finished in ivory coloured baked enamel, anodised bronze or aluminium unless otherwise specified.

5.2   		Cover plates shall overlap the outlet to cover wall imperfections.

5.3	Cover plates shall comply with SANS 1084.

SECTION C11

# C.11  UNSWITCHED AND SWITCHED SOCKET-OUTLETS

# 1.	GENERAL

This section covers the requirements for unswitched and switched socket-outlets for use in general installations under normal environmental conditions.

# 2.	FLUSH AND SURFACE MOUNTED SWITCHED SOCKETS

2.1	All switched socket-outlets shall be suitable for mounting in 100 x 100 x 50mm or 100 x 50 x 50mm boxes, shall comply with SANS 164.

2.2   	Switches shall be of the tumbler operated microgap type rated at 16A, 220/250V.

2.3   	Terminals shall be enclosed for safe wiring.

2.4   	Contacts shall be of silver material.

2.5   	Safety shutters shall be provided on live and neutral openings.

2.6   	The yoke strap shall be slotted to allow for easy alignment

2.7   	The covers of surface mounted switched socket shall have toggle protectors.

2.8   	Miniature circuit-breakers shall be used in lieu of a switch where specified.

2.9   	Where 13A flat pin switched socket-outlets are specified, these shall comply with BS 1363.

# 3.   	WATERTIGHT SWITCHED SOCKETS

3.1   	The housing of watertight switched sockets shall be of galvanised cast iron or die cast aluminium with watertight machined joints.

3.2   	The switch shall have a porcelain base and a quick-acting spring mechanism and shall be rated at 16A. 220/250V.

3.3   	The ON/OFF positions shall be clearly marked on the switch housing.

3.4   	The socket openings shall be rendered watertight by means of a gasketed cover plate which is screwed onto the body of the unit. The cover plate shall be secured to the body of the unit by means of a chain.

# 4.   	UNSWITCHED SOCKET-OUTLETS

4.1   	Unswitched socket-outlets shall only be used in the case of 5A, 220/250V, 3-pin socket-outlets intended for the connection of recessed light fittings installed in false ceilings.

4.2   	The socket-outlets shall have shuttered live and neutral openings.

  - The socket-outlets shall be suitable for installation in pre-punched wiring channels. deep  round conduit boxes, 100 x 50 x 50mm or 100 x 100 x 50mm boxes.

# 5.  	THREE-PHASE SWITCHED SOCKET-OUTLETS

5.1   	Three-phase switched socket-outlets shall have 5 pins, one for each phase, neutral and earth. The current rating shall be as specified in the Detail Technical Specification.

5.2   	The units shall be interlocked to prevent switching on if the plug top is not installed.

  - The units shall be supplied complete with plug top.

5.4   	The live terminals shall be shrouded and shall be completely safe when the plug top is removed.

5.5  	Samples shall be submitted to SARS for approval prior to the installation.

# 6.    	SHAVER SOCKETS

6.1   	Shaver sockets shall comprise a double wound isolating transformer rated at 20 VA.

6.2   	A three hole system shall be provided to provide for 115 V or 230V systems and also to cater for various types of shaver plugs.

6.3   	Insertion of a shaver plug shall automatically switch on the unit by energising the primary side of the isolating transformer. Removal shall switch it off.

6.4   	The unit shall be protected against overload by a thermal overload device.

6.5	The unit shall comply with BS 3052.

SECTION C12

# C.12  LUMINAIRES FOR INTERIOR AND EXTERIOR APPLICATIONS

# C.12.1  TUBULAR FLUORESCENT LAMP LUMINAIRES FOR INTERIOR APPLICATIONS

# 1.   	SCOPE

This specification covers the requirements for fluorescent luminaires using tubular fluorescent lamps for general indoor use. The types of luminaires covered are open-channel, industrial, decorative and recessed types and includes luminaires with one or more lamps with standard wattage ratings as specified in the project specification. Luminaires for use in special applications or atmospheres are not included in this specification. .

# 2.   	GENERAL

2.1    	To promote work creation in South Africa, the luminaire should preferably be manufactured within the Republic of South Africa and should have a local content of at least 50%.

2.2    	If the luminaire offered is of foreign origin, full specifications on technical performance and quality must be submitted and full reasons shall be given why the unit had to be imported.

2.3   	A sample luminaire shall be provided for evaluation and approval by the Electrical Engineer prior to installation.

2.4   	Luminaires, associated equipment and control gear shall be new and unused and shall be supplied complete with lamps, control gear, diffusers, mounting brackets, etc. and shall be delivered to site in a protective covering.

2.5   	Lamps shall be delivered separately.

# 3.    	STANDARDS

The following standard specifications of the South-African National Standards shall apply to this luminaire specification:

3.1	SANS 1119:		Interior luminaires for fluorescent lamps.

3.2	SANS 1250:		Capacitors for use with fluorescent and other discharge lamp ballasts.

3.3	SANS 890:		Ballasts for fluorescent lamps.

3.4	SANS 1464:		Safety of luminaires.

3.5	SANS 1479:		Glow starters for fluorescent lamps.

3.6	IEC 400:			Lamp holders for tubular fluorescent lamps.

3.7	SANS 1041:		Tubular fluorescent lamps for general service.

3.8 	SANS VC 8031:		Coatings applied by the powder-coating process.

3.9	SANS 783:		Baked enamels.

3.10	SANS 10142:		The wiring of Premises

Any standard referred to in the above specifications.

# 4.	PHYSICAL AND ENVIRONMENTAL REQUIREMENTS

4.1   	AREAS OF APPLICATION: The luminaires are intended for standard indoor use in buildings under the control of SARS.

4.2    	FIXING: The luminaires shall be suitable for mounting in or against ceilings as described in the project specification.

  - ENVIRONMENTAL: Unless otherwise specified in the detail specification the luminaires shall be suitable for operation in ambient temperatures between -10°C and +25°C.

4.4   	SAFETY: The luminaire shall bear the SANS 1464 safety mark.

4.5   	NOISE: Noisy ballasts will not be accepted and shall be replaced at no cost to SARS. All ballasts shall comply with the requirements of the latest edition of SANS 890. Part 1.

# 5.   	GENERAL TECHNICAL REQUIREMENTS

## 5.1	GENERAL

5.1.1	Tubular fluorescent lamp luminaires shall comply fully with SANS 1119 and all amendments as well as the additional requirements of this specification. Luminaires shall bear the SANS mark, or at least have a SANS Certificate of Compliance.

5.1.2 	SARS reserves the right to have samples of luminaires offered tested by the SANS for compliance with SANS 1119. If a sample luminaire is found not to comply with SANS 1119 the cost of such tests shall be borne by the Tenderer.

## 5.2  	CONSTRUCTION

5.2.1 	A luminaire shall consist of a ventilated body manufactured of cold rolled sheet steel not less than 0,8mm thick, suitably braced or stiffened to prevent distortion. The body shall be of sufficient strength for the mounting of the entire luminaire.

5.2.2 	The luminaire shall be designed to accommodate the control gear, wiring, lamp holders and, where applicable, the diffuser and reflectors. It shall be possible to reach the control gear without disconnecting wiring or removing the luminaire.

5.2.3 	Except for mounting holes and/or slots and the required openings in air-return luminaires. the back of the body channel shall be closed over the full length of the luminaire.

5.2.4 	Suitable knockouts shall be provided in the rear of the luminaire body for wire entry.

5.2.5 	All components, including screws, bolts and nuts utilised in the construction of the luminaire or fixing of its components, shall be corrosion proof. Cadmium plated or stainless steel materials are preferred.

## 5.3	INTERNAL WIRING

    - Luminaires shall be completely wired internally. Conductors shall be protected with grommets where they pass through holes in the body.

5.3.2 	The wiring shall be totally metal enclosed to prevent any possible contact with live components while changing lamps.

5.3.3 	The conductor insulation shall be rated to withstand the temperature inside the luminaire body without deterioration.

    - The wiring shall terminate on a suitable terminal block having screw down plates bearing on the wires. Terminals where screws bear down directly on wires will not be acceptable.

5.3.5 	An earth terminal, welded to the luminaire body, shall be provided. To ensure good earth continuity the earth terminal shall not be spray painted. The earth conductor shall be connected to this terminal by means of a crimped lug.

## 5.4  	LAMP HOLDERS

Lamp holders shall preferably be of the telescopic spring-loaded type. Where twist-lock type lamp holders are provided, the mounting of the holders shall be able to accommodate the tolerances experienced in the length of lamps and in the manufacture of luminaires.

## 5.5   	CONTROL GEAR

    - The control gear, ballasts, capacitors and starters shall be designed and manufactured to suit the control circuitry adopted. All luminaires shall operate on a switch-start basis.

5.5.2 	Ballasts shall comply with SANS 890 and SANS 891, suitable for operation on 220V to 250V, 50Hz supplies.

5.5.3 	Ballasts shall further be suitable for the particular luminaire to ensure that the thermal limits specified in paragraph 3.5 of SANS 1119 are not exceeded.

5.5.4 	Starters shall comply with SANS 1479 or with BS 3772 if it is not covered by SANS 1479. Starters with metal cans shall contain integral earthing facilities to earth the can upon insertion.

5.5.5 	Starters shall be accessible from the outside of the luminaire, and the replacement of the starter shall not necessitate the removal of lamps.

## 5.6	CAPACITORS

Capacitors shall comply with SANS 1250. The power factor of each complete fitting shall be corrected to at least 0,85.

## 5.7   	LAMPS

5.7.1 	Fluorescent lamps shall be suitable for the control circuitry used. Lamps shall comply with SANS 1041.

    - If no colour is specified in the Detail Technical Specification, the light colour shall correspond to colour 2 (4 300K) of SANS 1041.

    - Lamps of the same colour shall be provided for an entire installation unless specified to the contrary.

5.7.4	 There shall be no visible flicker in the lamps and lamps shall readily strike when switched on. Faulty lamps or ballasts shall be replaced at no cost to SARS.

# 6.   	PHOTOMETRIC DATA

Photometric data sheets of the luminaire as prepared by a laboratory that complies with SANS requirements, shall be submitted with the luminaire.

# 7.   	TECHNICAL INFORMATION

The Tenderer shall include full technical particulars regarding the luminaire offered with the tender.

# 8.   	CHANNEL LUMINAIRE

8.1    	Channel luminaires shall consist of a ventilated, enclosed channel body with one or more lamps as specified in the project specification. The channel body shall house the ballast, capacitor, terminals and internal wiring.

8.2    	Provision shall be made for the addition of reflector wings and/or diffusers.

8.3   	Three sets of mounting slots and knock-outs suitable for mounting onto standard round conduit boxes and/or 20mm diameter conduit pendant rods, shall be provided in the rear of the channel, one in the centre and one approximately one sixth from each end.

8.4   	A knockout suitable for a 20mm diameter conduit entry shall be provided at each end of the channel. The distance between the back of the luminaire and centre of the knockout shall be approximately 25mm.

  - The knockouts shall be positioned on the centre line of the channel.

8.6   	The body channel shall incorporate a removable cover acting as a reflector, manufactured of cold rolled steel, not less than 0,8mm thick, designed and mounted to completely cover the interior of the body channel and its contents and extending over the full length of the luminaire up to the lamp holders.

8.7   	The reflector shall be firmly held in position with a latching device consisting of knurled, coin slot, captive screws. Plastic, used as a spring mechanism, is not acceptable as a fixing device for reflectors. The action of the latching device shall not deteriorate due to use and/or ageing.

# 9.    	INDUSTRIAL LUMINAIRES

  - Industrial type luminaires shall consist of a basic channel luminaire fitted with detachable side reflectors.

9.2   	The reflectors shall be manufactured of cold rolled steel, not less than 0,8mm thick.

  - The reflectors shall be designed to improve the downward light output ratio and decrease the upward light output ratio to a value of less than 2%.

# 10.	DECORATIVE LUMINAIRES

10.1	Decorative luminaires shall incorporate an injection moulded prismatic acrylic diffuser or a high-grade optical reflector covering the entire reflecting surface of the luminaire.

10.2 	The diffuser shall be hinged or easily removable for maintenance and lamp replacement. Optical reflectors shall be hinged.

10.3  	Decorative luminaires with diffusers shall be constructed and so installed to prevent the ingress of dust and insects.

10.4  	Highly polished reflectors shall be protected and carefully handled and to prevent fingerprints showing on the surface.

10.5  	Surface mounted luminaires on suspended ceilings shall be arranged to suit the grid and shall fit tightly against the ceiling.

# 11.   	RECESSED LUMINAIRES

11.1 	Recessed luminaires shall be suitable for mounting in the ceiling structure specified in the project specification.

11.2  	The attachment of the prismatic diffuser or reflector shall be similar to that specified in paragraph 10 above.

11.3  	The djffuser or reflector shall fit flush with the ceiling and the only visible portion shall be the reflector or diffuser.

11.4  	Should the luminaire be so designed that a surrounding frame is visible, then this frame shall be manufactured of anodised aluminium. The frame shall form a neat trim with the ceiling. The comers of the surrounding frame shall be mitred and reinforced.

# 12.   	LOW-BRIGHTNESS LUMINAIRES

12.1 	The luminaire shall be provided with an aluminium louver with V-shaped longitudinal vanes and extruded stepped cross-shielding plates.

12.2  	Louvers shall be constructed from high purity aluminium (99,98%), chemically brightened and anodised.

12.3 	The total Light Output Ratio (LOR) shall be 62% or better. In the plane between 60 and 90 (from the vertical), the LOR shall be below 3%.

# 13.   	LOW GLARE LUMINAIRES

13.1	The luminaire shall be provided with a die-formed, bright anodised high-purity aluminium (99,98%) louver with parabolic reflecting surfaces in both directions.

  - The total LOR shall be 62% or better. In the plane between 60 and 90(from the vertical), the LOR shall be less than 1,3%

# 14.	LUMINAIRES FOR USE IN AREAS WITH VISUAL DISPLAY TERMINALS

14.1	The luminaire shall have anodised specular louvers to provide the brightness control required for this type of application.

14.2 	At angles between 60 and 90 (from the vertical) the luminance shall not exceed 200cd/m2.

14.3	At the above angles the LOR shall be less than 0,6%. At angle between the vertical and 60 the LOR shall be 61% or better.

SECTION C12.3

# C12.3  BULKHEAD LUMINAIRES FOR USE WITH COMPACT FLUORESCENT OR TUNGSTEN FILAMENT LAMPS FOR INTERIOR AND EXTERIOR APPLICATIONS

# 1.   	SCOPE

This specification covers the requirements for bulkhead type luminaires, using compact fluorescent or tungsten filament lamps, for general indoor and outdoor use. The types of luminaires covered are decorative round, rectangular or square surface-mounted and recessed types and include luminaires with one or more lamps with standard wattage ratings as specified in the project specification. Luminaires for use in special applications or atmospheres are not included in this specification.

# 2.   	GENERAL

2.1   	To promote work creation in South Africa, the luminaire should preferably be manufactured within the Republic of South Africa and should have a local content of at least 50%.

2.2   	If the luminaire offered is of foreign origin, full specifications on technical performance and quality must be submitted and full reasons shall be given why the unit had to be imported.

2.3   	A sample luminaire shall be provided for evaluation and approval by the Electrical Engineer prior to installation.

  - Luminaires. associated equipment and control gear shall be new and unused and shall be supplied complete with lamps, control gear, diffusers, mounting brackets, etc. and shall be delivered to site in a protective covering.

2.5   	Lamps shall be delivered separately.

# 3.    	STANDARDS

The following standard specifications of the South-African National Standards and the International Electrotechnical Commission shall apply to this luminaire specification:

3.1	SANS1119: 				Interior luminaires for fluorescent lamps. Note: The latest

amendments 	whereby luminaires with compact                                                                                             fluorescent lamps are covered, shall apply.

3.2   	SANS 1250:				Capacitors for use with fluorescent and other discharge

lamp ballasts.

3.3   	SANS 890, IEC 920 & IEC 921:		Ballasts for fluorescent lamps.

3.4   	SANS 1464:				Safety of luminaires.

3.5   	SANS 1479:				Glow starters for fluorescent lamps.

3.6   	IEC 400:     				Lamp holders for tubular fluorescent lamps.

3.7   	SANS 1041, IEC 81 & IEC 901:       	Tubular fluorescent lamps for general service.

3.8  	SANS 1247:        			Coatings applied by the powder-coating process.

3.9   	SANS 783:         				Baked enamels.

3.10 	SANS 10142:        			The wiring of Premises

3.11  	SANS 56:         				Incandescent lamps

3.12	Any standard referred to in the above specifications.

# 4.   	PHYSICAL AND ENVIRONMENTAL REQUIREMENTS

4.1   	AREAS OF APPLICATION: The luminaires are intended for standard indoor and exterior use in buildings under the control of SARS.

4.2    	FIXING: The luminaires shall be suitable for mounting against ceilings or walls as described in the project specification.

  - ENVIRONMENTAL: Unless otherwise specified in the detail specification the luminaires shall be suitable for operation in ambient temperatures between -10°C and +45°C.

4.4   	SAFETY: The luminaire shall bear the SANS 1464 safety mark.

  - NOISE: Noisy ballasts will not be accepted and shall be replaced at no cost to SARS. All ballasts shall comply with the requirements of the latest edition of SANS 890, Part 1 or IEC 920 and IEC 921.

# 5.	GENERAL TECHNICAL REQUIREMENTS

## 5.1   	General

5.1.1 	Compact fluorescent lamp luminaires shall comply fully with SANS 1119 and all amendments as well as the additional requirements of this specification. Luminaires. which bear the SANS mark, are preferred. Luminaires shall at least have an SANS Certificate of Compliance.

5.1.2 	SARS reserves the right to have samples of luminaires offered tested by the SANS for compliance with SANS 1119. If a sample luminaire is found not to comply with SANS 1119 the cost of such tests shall be borne by the Tenderer.

5.1.3 	Luminaires for tungsten filament lamps shall not materially differ from those for compact fluorescent lamps, but shall be capable of dissipating the extra heat generated without deterioration in the luminaire materials.

## 5.2    	Construction

5.2.1 	A luminaire shall consist of a ventilated body manufactured from die-cast aluminium. The body shall be of sufficient, strength for the mounting of the entire luminaire.

5.2.2 	The luminaire shall be designed to accommodate the control gear, wiring, lamp holders, the diffuser and reflectors. It shall be possible to reach the control gear without disconnecting wiring or removing the luminaire.

5.2.3 	Except for mounting holes and/or slots, the back of the body shall be closed over the full extent of the luminaire.

5.2.4 	Suitable knockouts shall be provided in the rear of the luminaire body for wire entry.

    - All components, including screws, bolts and nuts utilised in the construction of the luminaire or fixing of its components, shall be corrosion proof. Cadmium plated or stainless steel materials are preferred.

5.2.6 	The luminaire shall, as an option, be available with a high-pressure die-cast aluminium skirt, which shall be designed in such a way that it covers the base completely when mounted. The skirt shall be mounted onto the body by means of at least three screws

## 5.3    	Internal wiring

5.3.1 	Luminaires shall be completely wired internally. Conductors shall be protected with grommets where they pass through holes in the body.

5.3.2 	The wiring shall be totally metal enclosed to prevent any possible contact with live components while changing lamps.

5.3.3 	The conductor insulation shall be rated to withstand the temperature inside the luminaire body without deterioration.

5.3.4 	The wiring shall terminate on a suitable terminal block having screw down plates bearing on the wires. Terminals where screws bear down directly on wires will not be acceptable.

5.3.5	An earth terminal, welded to the luminaire body, shall be provided. To ensure good earth continuity the earth terminal shall not be spray painted. The earth conductor shall be connected to this terminal by means of a crimped lug.

## 5.4   	Control gear

5.5.1 	The control gear, ballasts, capacitors and starters shall be designed and manufactured to suit the control circuitry adopted. All fluorescent luminaires shall operate on a switch-start basis where external starters are employed.

5.5.2 	Ballasts shall comply with SANS 890 & SANS 891, or IEC 920 & IEC 921 as applicable and shall be suitable for operation on 220V to 250V, 50Hz supplies.

5.5.3 	Ballasts shall further be suitable for the particular luminaire to ensure that the thermal limits specified in paragraph 3.5 of SANS 1119 are not exceeded.

5.5.4 	Starters shall comply with SANS 1479 or with BS 3772 if it is not covered by SANS 1479. Starters with metal cans shall contain integral earthing facilities to earth the can upon insertion.

    - Starters shall be accessible from the outside of the luminaire, and the replacement of the starter shall not necessitate the removal of lamps.

    - The luminaire reflector shall act as the gear/mounting tray and shall be manufactured from sheet steel at least 0,7mm thick. The gear tray shall preferably be white epoxy powder coated after all the cut-outs and holes have been made on the tray. The tray shall be mounted to the body of the luminaire by means of screws and the tray shall be provided with a hole through which the screw head can pass plus a slot of the same width as the screw thickness so that the tray can be removed without removing the screws completely.

5.5.7 	The gear tray shall be equipped with the components suitable for the luminaires specified in the project specification.

## 5.6   	Capacitors

Capacitors shall comply with SANS 1250. The power factor of each complete fitting shall be corrected to at least 0,85.

## 5.7  	Lamps

5.7.1 	Fluorescent lamps shall be suitable for the control circuitry used. Lamps shall comply with the applicable clauses of SANS 1041 and, where it does not apply, the lamps shall comply with IEC 81 or IEC 901.

5.7.2 	If no colour is specified in the Detail Technical Specification, the light colour shall correspond to colour 2 (4 300K) of SANS 1041.

5.7.3 	Lamps of the same colour shall be provided for an entire installation unless specified to the contrary.

5.7.4	There shall be no visible flicker in the lamps and lamps shall readily strike when switched on. Faulty lamps or ballasts shall be replaced at no cost to SARS.

## 5.8    	Diffuser

5.8.1 	The diffuser shall consist of a high-impact resistant ultra-violet stabilised acrylic moulding. The diffuser shall be either transparent or opaque as described in the project specification. Where transparent diffusers are required, these shall be moulded with internal prismatic refractors and the outer surface shall be smooth.

5.8.2 	The diffuser shall be mounted to the body by means of an external mounting ring and at least three screws, which should preferably not pass through the diffuser body as well. A silicon sponge gasket which fits into a groove on the diffuser shall be used to allow breathing of the luminaire whilst prohibiting the ingress of insects.

# 6.   	PHOTOMETRIC DATA

Photometric data sheets of the luminaire as prepared by a laboratory that complies with SANS requirements, shall be submitted with the luminaire.

# 7.    	TECHNICAL INFORMATION

The Tenderer shall include full technical particulars regarding the luminaire offered with the tender.

SECTION C15

# C.15  BUSBARS (RISING AND OVERHEAD FOR VOLTAGES UP TO 1 kV)

# 1.	GENERAL

1.1   	Busbars shall be designed and manufactured in compliance with SANS 1473 and SANS 1195.

1.2   	Rising and overhead busbar trunking shall be fully enclosed in a sheet metal duct which shall form part of the busbar support.

1.3   	The entire busbar system shall be manufactured in sections. It shall be possible to remove intermediate sections without having to dismantle or remove adjacent sections.

# 2.   	BUSBAR ENCLOSURE

2.1   	The metal enclosure shall form an integral part of the bus section and shall be of the same length as the conducting sections of the busbar. Bus sections shall be securely fixed at each joint by means of bolted fishplates.

2.2   	The busbar shall be splash proof and vermin proof and adequately ventilated.

2.3   	Each bus section shall have at least four fixing points. These points shall be capable of accepting M10 bolts with hexagonal heads.

2.4   	The covers of the busbar trunking shall be firmly secure to one chassis or framework by at least four points per section.

2.5   	Self-tapping screws are not acceptable as a means of fixing or securing any part or component on busbar trunking.

2.6   	Suitable locking devices, i.e. spring washers or locknuts, shall be incorporated with all threaded parts to withstand vibration and stresses caused under normal and fault conditions.'

2.7   	Busbar covers shall be so designed to facilitate removal of the covers after installation. Sections of the busbars which pass through walls and floors shall have separate covers. This is necessary because the walls and floors will be built up to the busbar enclosure as a fire barrier.

# 3.	PAINT FINISH

Metal components of the framework and panels of the busbar trunking shall be painted. The colour shall be "LIGHT ORANGE", colour B26 of SANS 1091.

# 4.   	BUSBARS

## 4.1  	General

Busbars shall be manufactured of solid drawn high conductivity copper with a rectangular cross section in accordance with SANS 1473 and SANS 1195 and BS 159 and BS 1433 where applicable.

4.1.2 	The voltage and current rating of the busbar shall comply with the Detail Technical Specification.

4.1.3 	The current rating shall be indicated on a stamped metal label on each section of the busbar trunking as well as the name and address of the manufacturer.

## 4.2   	Voltage Rating

4.2.1 	The busbar system shall be designed to withstand the service voltage and the corresponding test voltage specified in SANS 1473.

4.2.2 	The minimum clearance between current carrying parts and other metal parts specified in SANS 1473 shall be maintained.

## 4.3   	Current Rating

4.3.1 	The maximum allowable temperature of busbars (including joints) carrying full load current in an ambient temperature as specified shall not exceed 80C, unless different ambient temperatures are specified, an ambient temperature of 35C shall be assumed with a maximum temperature increase of 45C.

4.3.2 	Table C15.2 may be used as a guide in determining busbar ratings where the distance between the phase busbars is at least the distance of the longer side of the cross-section with a minimum spacing of 50mm and at least 150mm from the sheet metal enclosure. It is however essential that the busbar manufacturer shall make due allowance for the "proximity and skin" effects, the effect of ferrous enclosures, ventilation etc. and for the arrangement used in his busbar design. Manufacturers shall, where requested, prove that the busbar rating and enclosure design comply with the temperature rise specified above. The busbars can also be rated to DIN 43671 for unpainted busbars.

4.3.3 	Neutral busbars in three-phase, four wire supplies shall have the same dimensions as the phase busbars.

4.3.4 	Busbars may not be tapered. The rating of the bars shall be equal to the incoming current rating. In cases where the main switch is an isolator, the isolator rating may not be taken as the incoming current rating.

4.3.5 	In addition to the current rating busbars shall comply with the following fault level rating:

A = 8,2 x 1 x (t) 1/2

where

A =	minimum cross-section (mm2)

I   =  	prospective fault current (kA)

t   =  	maximum time in seconds required for protection equipment to clear the fault.

(Minimum allowable value for t = 0,2s).

4.3.6 		Where a busbar consists of two or more busbars per phase (laminations), the laminations shall be separated by a minimum distance of the thickness of one lamination. The laminations shall be clamped together with copper spacers at intervals not exceeding 450mm in order to equalise the current distribution in the laminations. The busbar ratings in Table C15.2 shall be multiplied by the factors shown in Table C15.1 to determine the total current rating per phase.

## 4.4   	Mounting

4.4.1 	Busbar sections shall be supported at a minimum of two points in each section.

Busbars shall be supported by resin bound synthetic wood panels or other suitable dielectric material. The surface of these supports shall be treated to prevent surface tracking. The supports shall be bolted securely to the framework and busbars shall fit tightly in the supports.

4.4.2 The rating and fixing of busbars shall be designed to withstand mechanical and temperature stresses during fault conditions. The busbar system shall withstand a fault current under test conditions of 20 times rated current for 1 second when applied :

(a) between all three phases,

(b) any two phases,

(c)  neutral and the adjacent phase, and

(d) earth conductor and nearest phase conductor.

4.4.3 	If no other methods are specified, the stresses under fault conditions shall be calculated as follows, taking into account correction factors for different configurations.

Mechanical stresses

F =  16 x I² x k    N/m

D x 10 000

where F = force (N/m)

I = maximum fault current (A RMS symm.)

d = spacing between bars (m)

k = space factor for rectangular bars (Fig. C15.1)

4.4.4 	The maximum allowable spacing of busbar supports for fault levels of 15 kA and more is 600mm.

## 4.5   	Bends

Busbars shall be radius edged where they change direction.

## 4.6   	Busbar Sections

Busbars shall be divided into sections (par. 1.3) and jointed to overlap for a distance equal to twice the width of the bar to prevent localised heating. Contact surfaces shall be tinned (acid-base flux may not be used) or silver-plated and bolted down with cadmium-plated bolts and nuts and spring washers with an applied torque in accordance with SANS 1473. Busbars shall be prepared for extension where they terminate at the ends of the trunking.

## 4.7   	Earth Busbar

4.7.1 	An earth busbar shall be installed in a convenient position along the entire length of the busbar.

4.7.2	The cross-sectional area of earth busbars shall be calculated in accordance with the following formula in IEC 439 with a minimum cross-section of 6,3 x 20mm:

S 	=	 I  x (t) 1/2

X    (d) 1/ 2

where S = 	cross-section (mm2)

I	 =   	the r.m.s. value of the current (A)

X 	=	 13 for Copper

t 	=	 operating time of protection equipment (s) (Minimum value = 0,2s)

dT 	= 	temperature rise (C) = 120C for insulated conductors = 180C for uninsulated

conductors

If t is between 2s and 5s, then dT may be increased in the same formula to:

dT 	= 	145C for insulated conductors

= 	215C for uninsulated conductors.

4.7.3 	In addition to the above considerations, the longer side of the earth busbar shall be at least twice the diameter of the largest bolt that wiil be fitted to the busbar.

4.7.4	The method of installation of the earth bar shall permit the connection of earth conductors at any point.

## 4.8   	Expansion Joints

4.8.1 	Expansion joints to allow for thermal expansion and contraction shall be provided at intervals not exceeding 10m to allow for a temperature variation from 0C to 90C.

4.8.2	These expansion joints shall be made with flexible braided copper strap or laminated copper foil with the same current carrying capacity as the rest of the busbar trunking.

4.8.3 	Connections to transformers and switchboards shall consist of similar flexible connections.

# 5.   	EARTHING OF METAL PARTS

5.1   	All non-current carrying metal parts of the busbar system, e.g. framework, panels, transformer cores, metal covers, etc. shall be bonded to the earth busbar.

5.2   	Provision shall be made at each fused take-off for a connection to the earth bar. This connection shall consist of a hole to accommodate one or more M10 bolts with nuts and washers and be prepared as described in par. 4.6.

# 6.   	BOLTS AND NUTS

Only cadmium-plated high tensile steel bolts and hexagonal nuts may be employed at busbar joints and connection points. All nuts shall be provided with spring washers or be of the "NYLOCK" type with washers. The largest possible size bolt that will fit into holes in lugs and fixing holes of equipment shall be used in every instance. Bolts shall be of sufficient length so that at least two but not more than five threads protrude beyond the nut.

# 7.   	ACCESSORIES AND CONNECTIONS

7.1   	All the accessories such as bends, cable connection boxes and fused take-offs shall be purpose-made and comply with the same specification as the busbars.

7.2   	The temperature rise of terminals or connections at incoming or outgoing cables may not exceed the temperature rating of the cable insulation. This final temperature shall not exceed 70ºC for PVC insulated cables.

7.3   	Where busbars terminating at the ends of switchboards are intended for future extension, these busbars shall be pre-drilled to accommodate the extension. Where pre-fitted space is specified for future equipment, the busbars in the proposed position shall be pre-drilled and nuts and bolts shall be provided to accommodate the future busbars or cables feeding the equipment.

# 8.   	FUSED TAKE-OFFS

8.1   	Fused take-offs for secondary supplies and equipment shall be supplied and installed in accordance with the Detail Technical Specification.

8. 2 	No connections shall be made to the main busbar without fuses. Take-offs shall comply with SANS 1473.

8.3  	The fuses of these take-offs shall comply with SARS's standard specification for "CARTRIDGE FUSES AND FUSE HOLDERS", Section C22.

# 9.   	FIRE BARRIERS

9.1   	Two fire barriers in the busbar trunking shall form an integral part of each section of rising busbars.

Non-flammable, non-conducting material such as asbestos-cement shall be used for this purpose.

9.3   	The fire barriers shall be placed to prevent the spreading of fire from one floor of a building to the next but not restrict the ventilation of the busbars.

9.4   	Overhead busbars shall be equipped with fire barriers where the busbars pass through walls or partitions from one room to another, in accordance with par. 3.5 of SANS 1473.

# 10. 	TESTING

10.1 	Completed busbars shall be subjected to a test voltage of 2,5 kV r.m.s. for 1 min. in accordance with SANS 1473.

10.2 	Where required, fault current tests in accordance with par. 4.4.2 above shall be conducted.

TABLE C15.1

DERATING FACTORS FOR LAMINATED BUSBARS

| Area of Cross Section (mm2) | No of parallel busbars per phase |  |  |
| --- | --- | --- | --- |
|  | 2 | 3 | 4 |
| 500 | 1,78 | 2,45 | 3,13 |
| 1 000 | 1.72 | 2,36 | 3,00 |
| 1 500 | 1,65 | 2,24 | 2,84 |
| 2000 | 1,60 | 2,16 | 2,70 |
| 2500 | 1,55 | 2,10 | 2,60 |
| 3000 | 1,52 | 2,02 | 2,52 |
| 3500 | 1,48 | 1,98 | 2,48 |
| 4000 | 1,44 | 1,96 | 2,45 |

TABLE C15.2

CURRENT RATING OF SINGLE COPPER BUSBARS (A)

| Width (mm) | Thickness (mm) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2,5 | 3.15 | 4,0 | 6,3 | 10 | 12,5 | 16 |
| 12,5 | 155 | 180 |  |  |  |  |  |
| 16 | 190 | 220 | 250 |  |  |  |  |
| 20 | 230 | 265 | 300 |  |  |  |  |
| 25 | 280 | 320 | 365 | 470 |  |  |  |
| 31,5 | 340 | 385 | 440 | 560 |  |  |  |
| 40 | 420 | 475 | 540 | 680 | 870 |  |  |
| 50 | 510 | 575 | 650 | 820 | 1030 | 1160 |  |
| 63 |  |  | 790 | 990 | 1240 | 1370 |  |
| 80 |  |  | 970 | 1200 | 1480 | 1640 |  |
| 100 |  |  | 1160 | 1430 | 1760 | 2180 |  |
| 125 |  |  |  | 1710 | 2100 | 2310 | 2570 |
| 160 |  |  |  | 2070 | 2530 | 2780 | 3090 |
| 200 |  |  |  |  |  | 3290 | 3660 |
| 250 |  |  |  |  |  | 3900 | 4300 |
| 315 |  |  |  |  |  | 4630 | 5120 |
| 400 |  |  |  |  |  |  | 6230 |

SECTION C16

# C.16  EARTHING ELECTRODES

# 1.	GENERAL

This section covers uncoated, coated and metal clad circular rod electrodes intended to provide an earth in soil for electrical and lightning arrestor systems.

# 2.	CATEGORY AND TYPE

2.1   	Only the following type of earth rods shall be used:

1(a) -        	Solid copper.

1(b) -         	Solid stainless steel.

2 (a) -       	 Solid steel with bonded copper protection.

2 (b) -         	Solid steel with plated copper protection.

2 (c) -        	Solid steel with a shrunk-on copper jacket.

3    -         	Solid steel with a shrunk-on stainless steel jacket.

4   -	      	Galvanised steel.

2.2   		Bare aluminium is not acceptable as an electrode material.

2.3   	All rods shall be solid and of circular cross section with length as specified in the Detail Technical Specification.

2.4   	The nominal diameter of the earthing rods shall not be less than 16mm unless the rods are specified for placing in pro-drilled holes in which event the minimum nominal diameter shall not be less than 12mm.

# 3.   	COUPLINGS AND CONDUCTOR CLAMPS

3.1   	Earthing electrodes shall be provided with (n-1) couplings where n = number of rods supplied.

3.2   	Rods designed for coupling by means of external sleeves shall be provided with an adequate quantity of hydrocarbon or silicon grease to be applied to the coupling before the joint is made.

3.3   	Rods designed for coupling by means of internal pins or splines shall be provided with thin-walled tubes and hydrocarbon or silicon grease to seal the joint.

3.4   	Conductor clamps shall be provided to suit the type and size of rods provided and the type and size of conductor specified in the Detail Technical Specification.

  - The material of the clamps shall be electrolytically compatible with the rod and conductor materials.

3.6   	Where brazed or welded connections are specified, the supplier of the rods shall stipulate at least two types of metals which are compatible with the rod and conductor materials.

3.7	An adequate number of driving caps or bolts shall be supplied with the rods to protect the ends of the earthing rods whilst being driven into hard soil.

SECTION C17

# C.17  SWITCHBOARDS (Up to 1 kV)

# 1.	GENERAL

## 1.1	Scope

This section covers the manufacturing and testing of flush mounted, surface mounted and floor standing switchboards for general installations in normal environmental conditions and for system voltages up to 1 kV.

## 1.2   	Size

All switchboards shall be of ample size to accommodate the specified switchgear and provide space for future switchgear. For every 4 (or part of 4) 5kA circuit-breakers on a switchboard, space for an additional 5kA circuit breaker shall be allowed unless future space requirements are dearly specified. For circuit breakers above 5kA, this factor shall be 15%. The clearance between adjoining switchgear openings shall be as specified in par. 6.2.

## 1.3   	External Dimensions

The maximum allowable height of free standing switchboards is 2,2m. Cubicle type boards may be up to 2,4m high if they can be fully dismantled into individual cubicles. Where, due to space restrictions, a board exceeds 2,4m in height, equipment not normally requiring access, shall be installed in the top section, enabling equipment normally requiring access to be installed lower down in the board. All other specified external dimensions for switchboards shall be strictly adhered to. If the clearances specified in par. 6.2 cannot be adhered to as a result of restricting external dimensions, the Contractor shall obtain the approval of SARS before manufacturing the switchboards.

## 1.4   	Moisture and Vermin

All switchboards shall be rendered moisture proof and vermin proof and shall be adequately ventilated. Refer to par. 4.10 and 4.11.

## 1.5	Load Balance

The load shall be balanced as equally as possible across multiphase supplies.

# 2.   	CONSTRUCTION OF FLUSH MOUNTED SWITCHBOARDS

## 2.1   	Standard

Flush mounted switchboards shall comply fully with SANS 1765. Unless the depths of the switchboards are specified, the depths shall be determined in accordance with par. 6.

## 2.2	Expanded Metal

Where switchboards are to be built into 115mm thick walls, expanded metal shall be spot-welded to the rear of the bonding trays. The expanded metal shall protrude at least 75mm on each tray side to prevent plaster from cracking.

## 2.3	Knock-outs

Knock-outs shall be provided in the top and bottom ends of each switchboard tray to allow for the installation of conduits for the specified and future circuits. Knock-outs shall be provided for an equal number of 20mm and 25mm dia. conduits.

## 2.4		Panel

Front panels shall have machine punched slots for housing the specified and future flush mounted switchgear. The distance between the inside of the closed doors and the panel shall not be less than 20mm. No equipment may be mounted on the panel unless the panel is permanently hinged to the switchboard frame.

## 2.5   	Fixing of Front Panels

The front panel shall be secured to the architrave frame by means of 6mm studs and chromium-plated hexagonal domed nuts, hank nuts or captive fasteners. Alternatively the panel may be secured to the architrave frame by means of two pins at the bottom and a latch or lock at the top of the panel. Self-tapping screws will not be allowed. All front panels shall be provided with a minimum of one chrome plated handle.

## 2.6   	Door Handles and Catches

Switchboard doors shall be equipped with handles and catches. Locks shall only be provided when specified. In all cases where lockable doors are required and in all cases where the switchboard doors are higher or wider than 450mm, handles consisting of a push-button-and-handle combination with spring loaded catch or rotary handle-and-catch combination shall be installed. Switchboard doors smaller than 450mm in height and width may be equipped with spring loaded flush mounted ring type latches. Square key operated catches are not acceptable unless specified.

# 3.   	CONSTRUCTION OF SURFACE MOUNTED SWITCHBOARDS

## 3.1   	Standard

Surface mounted switchboards shall comply with SANS 1765.

## 3.2   	Switchboard Tray

Surface mounted switchboards shall be equipped with a 1,6mm minimum sheet steel reinforced tray suitably braced and stiffened to carry the chassis, door and equipment. Lugs to secure the switchboard to a vertical surface shall be provided.

## 3.3	Construction

All joints shall be welded or securely bolted. The tray shall be square and neatly finished without protrusions. The front tray sides shall be rounded with an edge of at least 20mm to accommodate flush doors.

## 3.4   	Chassis

A sheet steel chassis for the mounting of equipment shall be bolted to the tray and shall comply with the requirements of par. 6.1 and 6.3.

## 3.5  	Front Panel and Door

The front panel and door shall comply with par. 2.4 to 2.6 above. Doors shall fit flush in the tray when closed.

## 3.6   	Dimensions

Unless the depth of the switchboards is specified, the dimensions shall be determined in accordance with the requirements of par. 6.2 and 6.3.

# 4.   	CONSTRUCTION OF FREE STANDING SWITCH BOARDS

## 4.1	Framework

A metal framework for free standing switchboards shall be manufactured from angle iron. channel iron or 2mm minimum folded metal. A solid U-channel base frame, sufficiently braced to support all equipment and span floor trenches and access holes shall be provided. Switchboards shall be of cubicle design with 2mm side panels forming divisions between cubicles. The maximum allowable cubicle width is 1,5m. (Refer also to par. 4.7). Joints shall be non-continuously butt-welded. Welds shall be ground smooth and the joint wiped with plumber's metal in order to provide a smooth finish. Switchboards wider than 2m shall be fitted with screwed eye-bolts attached to the framework to facilitate loading and transportation of the board.

## 4.2   	Rear and Side Panels

The rear panels shall be removable and shall be manufactured from 2mm minimum sheet steel. The panels shall have returned edges which are recessed in the frame or which fit over lips on the switchboard frame. The panels shall be secured to the frame by means of studs and chromium-plated hexagonal domed brass nuts or hank nuts or captive fasteners equal or similar to "DZUS" or "CAMLOC". Where switchboards are intended for installation in vertical building ducts or against walls, the rear and side panels may consist of a single folded sheet which is either bolted or welded to the frame or which forms part of the folded metal frame.

## 4.3   	Front Panels

4.3.1	The front panels of floor standing switchboards shall preferably be hinged except where flush mounted equipment prevents this. Alternatively, panels shall be secured by means of the methods described in par. 2.5. The panels shall be arranged in multi-tiered fashion to allow for the logical grouping of equipment in accordance with par. 6.

4.3.2	The hinged front panels shall have a dished appearance with 20mm upturns which fit over a lip on the switchboard frame. Alternatively the hinged panels shall have folded edges and shall be fitted flush or slightly recessed in the switchboard frame. The latter method shall be used where doors are required. (Also refer to par. 4.6). Corners shall be welded and smoothed.

4.3.3	The panels shall be of 2mm minimum sheet steel with machine punched slots to allow for the flush mounting of instrumentation, switchgear toggles and operating handles. A minimum clearance of 50mm shall be maintained between the rear of equipment mounted on the panels (taking into account terminals or other projections) and the frame and chassis of the switchboard. Separate panels shall preferably be provided for the mounting of instrumentation and for covering flush mounted switchgear. Enclosed switchgear with front panels e.g. combination fuse-switch units, may be flush mounted in the board in lieu of separate hinged panels.

4.3.4	Hinged panels shall be suitably braced and stiffened to carry the weight of flush mounted equipment and to prevent warping.

4.3.5	Hinged panels with flush mounted equipment and panels higher than 600mm shall be supported by hinges of adequate strength to ensure smooth and reliable operation. 16mm pedestal or similar heavy duty hinges with single fixing bolts may be used on panels smaller than 600mm. On the larger panels long pedestal type hinges with two fixing bolts per hinge are preferred. Piano hinges are not acceptable for this application.

4.3.6	A tubular chromium-plated handle shall be fitted on each panel. The handle may be omitted if "DZUS" or "CAMLOC" fasteners are used.

4.3.7	Blanking plates shall be fitted over slots intended for future equipment. These plates shall be fixed in a manner which does not require the drilling of holes through the front panel. Dummy circuit-breakers may be fitted where applicable.

4.3.8	Front panels containing live equipment such as instrumentation or control switches, shall be bonded to the switchboard frame with a braided copper earth trap with an equivalent cross-sectional area of at least 4mm2.

## 4.4   	Securing of Front Panels

Hinged panels shall be secured in position by means of square key operated non-ferrous fasteners designed to draw the panels closed or similar quick-release fasteners. Self-tapping screws are not acceptable. Where non-hinged removable panels are specified, they shall be secured in position by means of 6mm studs and hexagonal chromed brass dome nuts and washers or hank nuts.  Non-hinged removable panels may alternatively be secured in position by means of two pins at the bottom and a latch or lock at the top.

## 4.5   	Chassis

A suitably braced chassis for the mounting of switchgear and equipment shall be firmly secured to the frame of the switchboard. The chassis shall be designed so that the switchgear can be installed in accordance with par. 6. Circuit-breakers and isolating switches which are not of the moulded-case air-break type and the insulators of busbars for ratings of 200 A and more may be secured directly to the framework. (Refer to par. 6.1).

## 4.6   	Doors

(a)	Doors need only be provided when specified. Doors shall be arranged in multi-tiered fashion to allow for the logical grouping of equipment in accordance with par. 6.

(b) 	Doors shall have a dished appearance with a minimum of 20mm upturns which fit over a lip on the switchboard frame or shall fit flush in the switchboard frame. Corners shall be welded and smoothed.

(c)  	Doors shall be of aluminium sheet steel with machine punched slots to allow for the flush mounting of instrumentation, control and protection equipment. Switchgear shall be flush mounted in the front panels behind the doors unless specified to the contrary. A minimum clearance of 50mm shall be allowed between the rear of equipment mounted on doors (including terminals and projections) and the frame, front panel and chassis.

(d)  	Doors shall be suitably braced and stiffened to carry the weight of the equipment and to prevent warping.

(e)  	Hinges for doors shall be provided as described in par. 4.3.5. At least three hinges shall be provided on doors higher than 1,2m.

(f)  	Doors shall be fitted with handles consisting of a pushbutton-and-handle combination with springloaded catch or a rotary handle-and-catch combination. Flush mounted ring type handles or square key operated latches are not acceptable. The same key shall fit all locks on the switchboard in cases where locks are required.

(g)  	Doors shall be fitted with hypalon or neoprene seals.

(h) 	Doors containing any electrical equipment shall be bonded to the switchboard frame with a braided copper earth w re with an equivalent cross-sectional area of at least 4mm2.

## 4.7   	Sections

For ease of transportation and to facilitate access to the allocated accommodation, switchboards may be dismantled into cubicles or sections. Each section shall be rigidly manufactured to ensure that damage to the switchgear will not occur during transportation and handling. Where required, switchboards shall have temporary wood or steel bracing to protect switchgear and facilitate handling.

## 4.8   	Grouping of Switchgear

The switchgear shall be logically arranged and grouped as described in par. 6. Depending upon the number and size of components, a common front panel may be installed over one or more groups of equipment. All equipment shall be installed in accordance with the requirements of par. 6.

## 4.9   	Cable Gland Plate

A cable gland plate shall be installed across the full width of each power cubicle at a minimum height of 300mm above the bottom of the switchboard to house the cable glands. A Steel cable channel or other approved support shall be provided to carry the weight of the cable and remove mechanical stress from the cable glands. A minimum distance as required by the bending radius of outgoing cables shall be provided between the lowest terminals of major equipment and the gland plate.

## 4.10 	Ventilation

Switchboards shall be property ventilated, especially cubicles containing contactors, transformers, motor starters, lighting dimmers and other heat producing equipment. Louvres shall be fitted to provide adequate upward or cross ventilation. All louvres shall be vermin proofed with 1,5mm brass mesh or perforated steel plate internally spot welded over the louvres. The internal ambient temperature shall not exceed 40ºC.

## 4.11 	Vermin Proofing

Free standing boards shall be protected against vermin, especially from below, where cables have to pass through the gland plate, rubber grommets shall be provided and enough non-hardening compound shall be delivered with the board so that these holes can be sealed properly after installation of the cables.

# 5.   	CONSTRUCTION OF MAIN LOW TENSION SWITCHBOARDS

Main low tension switchboards and sub-main low tension switchboards heavily equipped shall comply with par. 4.1 to 4.11 as well as the following exceptions or additions:

(a)	These boards shall be fully extensible with removable busbar cover plates in the side panels.

(b)	Doors shall not be supplied unless specifically called for.

(c)	Switchgear and equipment shall be installed in accordance with the requirements of par. 6.

(d)  	Provision for metering equipment shall be made in accordance with requirements of local authorities where applicable.

# 6.  	MOUNTING OF EQUIPMENT

6.1   	The mounting of equipment shall comply with SANS 1765 where applicable. Equipment to be mounted on the chassis shall be mounted by bolts, washers and nuts or by bolts screwed into tapped holes in the chassis plate. In the latter case the minimum thickness of the chassis plate shall be 2,5mm. The latter method shall not be used where boards will be subject to vibration or mechanical shocks. Self-tapping screws will not be accepted.

## 6.2   	Space Requirements

In designing the switchboards the following requirements shall be strictly adhered to:-

- A minimum of 50mm between any piece of equipment and the frame or internal partitioning. This minimum space is required on all sides of the equipment. In the case of a single row of single-pole circuit-breakers the spacing on one side row may be reduced to 25mm if the incoming side of the circuit-breakers is busbar connected.

- A minimum of 75mm between horizontal rows of equipment. The maximum outside dimensions of equipment shall be considered.

(c)  	Circuit-breakers up to a fault rating of 10 kA may be installed adjacent to each other. For higher ratings a minimum of 40mm shall be allowed between circuit-breakers or isolators.

(d)  	Sufficient space shall be provided for wiring allowing for the appropriate bending radius.

(e) 	Space for future equipment shall be allowed as described in par. 1.2.

## 6.3   	Mounting of Chassis

The chassis of flush mounted and smaller surface mounted boards shall be mounted in accordance with SANS 1765. For all free standing switchboards and surface mounted switchboards where the main switch rating exceeds 100 A (triple-pole), space for wiring shall be provided between the chassis and tray. This space shall be adequate to install the supply cable behind the chassis and terminate on the main switch without sharp bends in the cable cores.

## 6.4   	Grouping of equipment

6.4.1 	Equipment shall be arranged and grouped in logical fashion as follows:

(a)  	Main switch - to be installed either at the top or bottom of the board.

(b) 	Short circuit protection equipment - fuse gear or fuse-switches.

(c)  	Change-over contactors or other contactors controlling the supply.

(d) 	Motor supplies.

(e)  	Fuse-switches for outgoing circuits.

(f)   	Other circuits and equipment.

6.4.2	Where a portion of the equipment on the switchboard is supplied from a standby power source, the change-over contactor and the associated equipment shall be grouped in a separate compartment.

6.4.3 	Where earth leakage units are required, the associated circuit-breakers shall be installed adjacent to the unit.

## 6.5   	Mounting of Circuit-Breakers

All moulded-case circuit-breakers shall be flush mounted with only the toggles protruding. Miniature circuit-breakers may be installed in clip-in trays mounted on the frame. All other circuit-breakers shall be bolted to the chassis. Special provision shall be made for large main switches when designing the framework. Care shall be exercised that the rear studs of circuit-breakers are properly insulated from the steel chassis. Where necessary, insulating material shall be installed between the rear studs and the chassis. Circuit-breakers shall be installed so that the toggles are in the up position when "ON" and down when "OFF".

## 6.6   	Instrumentation

All metering instruments shall be flush mounted in the front panel or door. The rear terminals of instruments mounted on doors shall be covered with an insulating material to prevent accidental contact. Current transformers for metering shall be mounted so that the rating plate is clearly visible. Fuses for instrumentation shall be mounted in an easily accessible position and clearly marked.

## 6.7   	Mounting of Fuses

6.7.1	Fuse holders shall be mounted semi-recessed in the front panel so that fuses can readily be changed without removing the front panel. Busbar mounted fuses for instrumentation shall be used as far as possible.

6.7.2	Where equipment requiring fuses is specified on a board (fuse switches etc), a ruling shall be obtained from SARS on the quantity of spare fuses to be provided.

## 6.8   	Equipment in Main Boards

Equipment in main low tension switchboards and sub-main boards shall be grouped in individual compartments. Equipment shall be installed as follows:

6.8.1 	Rack-out type air circuit-breakers shall be mounted in the bottom section, flush behind the panel with the handle only protruding. If this is not possible, the panel shall be omitted and the air circuit-breakers installed behind a door.

6.8.2 	If the main switch is a moulded-case circuit-breaker or isolator it shall be flush mounted.

6.8.3	Contactors controlling the supply shall be installed behind separate front panels.

6.8.4 	All metering, protection and indicating equipment shall be clearly visible from the front of the board. Current transformer ratios and multiplication factors shall be clearly marked. Where doors are specified the equipment shall be installed flush in the doors and covered as described in par. 6.6.

6.8.5 	All circuit-breakers and fuses (with the exception of fuse-switches) may be grouped together behind one or more panels as described in par. 4.8.

6.8.6 	Fuses or fuse-switches providing back-up protection for circuit breakers, shall be grouped with the associated circuit-breakers. Exposed surfaces effuse-switches shall be of the same finish and colour as the rest of the board where practical.

## 6. 9 	Standby Supplies

6.9.1 	Where standby power from a diesel-generator set or other sources is available and has to be connected to some of the equipment on a switchboard, the switchboard shall be divided into separate sections with sheet metal divisions to isolate standby power and mains power sections.

6.9.2 	Standby and normal supply shall each have its own incoming isolator or circuit-breaker.

    - The two sections of the switchboard shall be labelled "ESSENTIAL" and "NON-ESSENTIAL" respectively.

6.9.4 	The front panels of standby and no-break supply sections shall be painted in distinctive colours as follows:

(a)	Normal supply      	"LIGHT ORANGE", 	colour B26 of SANS 1091

(b) 	Standby power     	"SIGNAL RED", 	colour All of SANS 1091

(c)      	No-break supply   	"DARK VIOLET", 	colour F06 or

"OLIVE GREEN".	colour H05 of SANS 1091

# 7. 	BUSBARS IN SWITCHBOARDS

## 7.1  	Application

7.1.1	Busbars shall be manufactured of solid drawn high conductivity copper with a rectangular cross-section in accordance with SANS 1473, SANS 1195 and BS 159 and BS 1433, where applicable.

7.1.2 	Although SANS 1473 refers only to overhead or rising busbars, busbars in switchboards shall comply with applicable sections of this specification especially as far as insulation and clearance values, creepage distance, joints, insulation resistance, dielectric strength, deflection test, absorption resistance and rated short time withstand current are concerned.

7.1.3 	Busbars shall be supplied for the following applications:

(a)  	Distribution of supply voltage.

(b)	Connection of equipment with ratings exceeding the current rating of 70mm2 conductors (par. 8.6).

(c)	Connection of outgoing circuits with current ratings in excess of that allowed for 70mm2 conductors (par. 7.8).

(d)	Collector bars for parallel cables (par. 8.1).

(e)	Connection bars for neutral conductors (par. 7.9).

(f) 	Earth busbars (par. 7.10).

(g)	Connections to miniature circuit-breakers (par. 8.6).

## 7.2   	See Part C15 for further details.

# 8.    	WIRING

## 8.1 	Cabling

Cables connected to incoming or outgoing circuits shall be terminated on the gland plate supplied for this purpose. (Refer to par. 4.9). Power cables up to and including 70mm2 may terminate on clamp type terminals where the clamping screws are not in direct contact with the conductor. Connection to the equipment can then be made with cables that are similarly connected to the clamp terminal. All power cables larger than 70mm2 terminate on busbars that are connected to the associated equipment. Parallel incoming or outgoing cables shall be connected to a collector busbar without crossing the conductors.

## 8.2   	Terminal Strips

External wiring for low voltage, control, interlocking, alarm, measuring and DC circuits shall terminate on numbered wiring terminals complying the with Department's standard specification for "WIRING TERMINALS", Section C9. The correct terminal size as recommended by the manufacturer for each conductor to be connected shall be used throughout. The terminal numbers shall appear on the wiring diagrams of the switchboard. Terminals for power wiring shall be separated from other terminals. Terminals for internal wiring shall not be interposed with terminals for external circuits. All connections to terminals shall be identified as described in par. 8.8. Where switchboards consist of separate sections, the control wiring passing between sections shall be terminated on strips in each section so that control wiring can be readily re-instated when reassembling the board.

## 8.3   	Current Ratings

The current rating of conductors for the internal wiring shall be sufficient for the maximum continuous current that can occur in the circuit. This value shall be determined from the circuit-breaker or fuse protection of the circuit.

TABLE 17.3

CURRENT RATING FOR INTERN

|  | CONDUCTOR RATING (A) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Nominal cross- |  |  |  |  |  |
| Section mm2 |  |  |  |  |  |
|  | Number of conductors in bunch |  |  |  |  |
|  | 1 | 2-3 | 4-5 | 6-9 | 10 and more |
| 2,5 | 28 | 25 | 22 | 19 | 16 |
| 4 | 37 | 33 | 30 | 26 | 22 |
| 6 | 47 | 42 | 38 | 33 | 28 |
| 10 | 64 | 54 | 51 | 44 | 38 |
| 16 | 85 | 76 | 68 | 59 | 51 |
| 25 | 112 | 101 | 89 | 78 | 67 |
| 35 | 138 | 124 | 110 | 96 | 88 |
| 50 | 172 | 154 | 137 | 120 | 103 |
| 70 | 213 | 191 | 170 | 149 | 127 |

The above table shall be applied for ambient temperatures up to 30ºC. (Refer to table 41.2 in VDE 0100). For higher ambient temperatures the values shall be derated as prescribed by SANS 10142. Table 10.

## 8.4   	Internal Wiring

(a)	Standard 600/1 000 V grade PVC-insulated stranded annealed copper conductors to SANS 1507 shall be employed for the internal power wiring of switchboards. The smallest conductor size to be used for power wiring in switchboards shall be 2.5mm2. Flexible cord of minimum size 1,0mm2 may be used for control wiring.

(b)	Where heat generating equipment is present and the internal temperature of the board is likely to exceed 50C, silicon-rubber insulated stranded conductors shall be used.

(c)	Wiring shall be arranged in horizontal and vertical rows and shall be bound with suitable plastic straps or installed in PVC wiring channels. Under no circumstances may PVC adhesive tape be used for the bunching of conductors or for the colour identification of conductors.

(d)	Bunched conductors shall be neatly formed to present a uniform appearance without twisting or crossing the conductors. Conductors leaving the harnesses shall be so arranged that they are adjacent to the chassis.

(e) 	Conductors to hinged panels and doors shall be secured on both the door and the frame and shall be looped between the two points. The loop shall be arranged to produce a twisting motion when the door is opened or closed. A flexible protection sleeve shall be installed over the conductors.

(f)	Where wiring channels are used, they shall be installed horizontally and vertically. Under no circumstances may power and control circuit wiring be installed in the same wiring channels. Channel shall not be more than 40% full.

(g) 	All wiring between different Panels within the same switchboard shall be installed in wiring channels.

(h)	Grommets shall be installed in each hole in the metalvvork through which conductors pass.

(i)	All wiring shall be installed away from terminals, clamps or other current carrying parts. Wiring shall also be kept away from exposed metal edges or shall be protected where they cross metal edges protected where they cross metal edges.

(k)	Conductors may be jointed at equipment terminals or numbered terminal strips only. No other connections are allowed.

(l)	Where conductors change direction, smooth bends shall be formed with a radius of at least 5 times the outside diameter of the conductor or harness.

(m)	Where screened cables are specified, the screening shall be earthed in the switchboard or control board only unless clearly specified to the contrary, Screened cables entering control boxes through pressed knock-outs, shall terminate in compression glands. Conductors shall as far as possible remain inside the screening at terminations. Where conductors have to separate from the screen, the braiding shall be separated and the conductors drawn through the braid without damaging the braiding. The conductors shall then be connected to their respective terminals and the screening smoothed and connected to the earth terminal.

(n)	Where neutral connections are looped between the terminals of instruments, it is essential that the two conductor ends be inserted into a common lug or ferrule and are crimped or soldered together in order that the neutral connection is not broken when the conductors are removed from one of the instruments.

(o)	Wiring should as far as possible be confined to the front portions of switchboards for ease of access. This requirement is important for wiring between smaller circuit-breakers and the associated main circuit-breaker as well as the wiring from circuit-breakers to lighting and socket-outlet circuits.

(p)	A maximum of two conductors will be allowed per equipment terminal. Where more conductors must be connected to the same equipment terminal (e.g. a main circuit-breaker feeding other circuit-breakers), stub busbars shall be provided for the various conductors. Refer also to par. 8.6.

## 8. 5 	Load End Connections

The supply end connections to all equipment shall under all circumstances be at the top and the load end connections at the bottom.

## 8.6   	Wiring to Circuit-breakers

Equipment with a rating exceeding the current rating of 70mm2 conductors shall be connected by means of busbars to the main busbars. Looped connections may only be installed for a maximum of two outgoing circuits. Where there are more than two outgoing circuits, busbars shall be used and equipment connected individually to the busbars. Where miniature circuit-breakers are mounted in continuous rows and supplied by busbars connected to each MCB. each busbar shall be supplied by a separate conductor. This conductor shall be connected to the busbar by means of a separate lug and not via an MCB terminal.

## 8.7  	Conductor Terminations

Conductors connected to terminals complying with SARS's standard specification for "WIRING TERMINALS". Section C9, need not be soldered or ferruled. Connections to circuit-breakers, isolators or contactors shall be made by one of the following methods:

(a)  	A ferrule of the correct size,

(b)  	soldering the end of the conductor, or

(c)  	winding a conductor strand tightly around the end to totally cover the end.

All conductors terminating on meters, fuse holders and other equipment with screwed terminals shall be fitted with lugs. The lugs shall be soldered or crimped to the end of the conductor. The correct amount of insulation shall be stripped from the end to fit into the terminal. Strands may not be cut from the end of the conductor.

## 8.8	Identification

8.8.1 	The colour of the conductors for all 220/250 V circuits shall correspond to the colour of the supply phase for that circuit. Neutral conductors shall be black.

8.8.2 	All other conductors in the board, supplying control circuits, etc. shall be coded in colours other than those specified above. A colour code shall be devised for each board and the colour code shall be shown on the wiring diagrams.

8.8.3	All conductors that terminate at wiring terminals and all conductors used for the internal wiring of the switchboard, shall further be identified at both ends by means of durable cable marking ferrules. PVC or other tape is not acceptable.

8.8.4 	The numbers on the markers shall be shown on the wiring diagrams.

# 10.  	LABELLING

10.1 	Care shall be taken to ensure that all equipment is fully labelled and that accurate descriptions and safety warning notices appear in both official languages.

## 10.2	Material

Engraved plastic or ivory sandwiched strips shall be used throughout. The strips shall bear white lettering on a black background for normal labels and red letters on a white or yellow background for danger notices.

## 10.3 	Main Switchboards

Main switchboards and sub-main switchboards shall be supplied with the following bilingual labels:

(a) 	Number and allocation of switchboard. Example:

CONTROL BOARD A4

BEHEERBORDA4

Lettering: at least 10 mm high prominent position. Label on the outside in a prominent position.

(b) 	Designation of busbar sections. Example:

BUSBAR SECTION 2

GELEISTAMSEKSIE2

Lettering: at least 10mm high. Label on the outside in a prominent position.

(c)	Designation of all switchgear including circuit-breakers, isolators, contactors, etc. If the current rating of circuit-breakers is not clearly marked on the equipment, the value shall be indicated on the engraved label. Example:

SUPPLY TO BOARD C3 TOEVOER NA BORD C3

PUMP SUPPLY

POMPTOEVOER

Letters at least 5mm high. Label on the outside of the switchboard.

(d) 	All other equipment including meters, instruments, indicator lights, switches, push-buttons, circuit-breakers, fuses, contactors, control relays, protection relays, etc. shall be identified. The function of the equipment and circuits shall be clearly indicated. The main switch shall be labelled as such and designated :

"SWITCH OFF IN CASE OF EMERGENCY"

"SKAKEL AF IN NOODGEVAL"

Flush mounted equipment within doors or front panels shall be identified with labels fixed to the doors or front panels respectively. The labels for equipment installed behind panels, shall be fixed to the chassis close to the equipment. If this equipment is positioned too close together to accommodate descriptive engraved labels, the equipment may be identified by a code or number on an engraved label which shall be fixed close to the equipment. The code number shall be identified on a legend card which shall be installed on the switchboard behind a plastic or other protective cover.

## 10.4	Other Switchboards

All equipment on switchboards shall be identified with the necessary bilingual labels.The circuit numbers shall appear at grouped single-pole circuit-breakers. The circuit numbers shall correspond to the circuit numbers on the final installation drawings. The above-mentioned circuits shall be identified on a legend card, which shall be installed on the inside of the switchboard door, or in any other position where it can conveniently be observed. All fuses, including instrument fuses, shall have labels stating function, fuse rating and duty or type where applicable. All other equipment shall be identified separately and their functions shall be clearly indicated.

## 10.5 	Fixing of Labels

10.5.1	Labels shall not be fixed to components or trunking but to doors, panels, chassis or other permanent structures of the switchboard.

10.5.2	Engraved strips shall be secured to facilitate a neat alteration of the designation of the labels. Sufficient fixing points shall be provided to prevent labels from warping. Labels in slotted holders shall be secured in position to prevent unauthorised removal. Labels may be secured by the use of brass bolts and nuts, self-tapping screws, slotted label holders or pop-rivets.

# 11 	TESTS

11.1 	SARS shall be notified when the mechanical construction of the switchboard, i.e. frame, panels and base frame, is complete in order that it may be inspected at the factory.

11.2	Function tests of all equipment, control and interlocking circuits shall be conducted to the satisfaction of SARS. Testing equipment and facilities including instruments, dummy loads and additional switchgear and cables shall be provided by the Contractor at no extra cost. SARS shall be notified in writing two weeks in advance of any test to be conducted, to allow its representative to be present at such tests. A complete report on the tests shall be handed to SARS.

# 12.	DRAWINGS

## 12.1 	Drawings for Approval

A set of three prints of the shop drawings for the switchboards shall be submitted to SARS for approval before the boards are manufactured. The following information shall be presented:

(a)	A complete wiring diagram of the equipment on the boards.

(b)  	A complete layout of the arrangement of the switchboards indicating all equipment dimensions and the construction of the boards. The positions and method of fixing and sizes of busbars shall be shown.

(c) 	All labelling information in both the official languages on a separate sheet.

(d) 	The make, catalogue number and capacity of all equipment such as isolators, circuit-breakers, fuses, contactors, etc.

The approval of drawings shall not relieve the Contractor of his responsibility to SARS to supply the switchboards according to the requirements of this Specification.

## 12.2 	Final Drawings

A complete set of "as-built" transparent drawings of all switchboards shall be submitted to SARS within two weeks after delivery of the boards. The following information shall be presented:

(a)	Item (a) to (d) of the previous paragraph.

(b) 	Terminal strip numbers, numbers and colours of conductors connected to the terminal strips and numbers and colours of the conductors utilised for the internal wiring.

(c) 	A separate schedule of all equipment.

## 12.3 	Manuals

Three sets of manuals for all specified main and sub-main switchboards shall be supplied to SARS at no extra cost. These manuals shall include the following information:

(a)   	Complete information on the operation of the equipment.

(b)   	Complete information for maintenance of the equipment.

(c)   	Brochures and ordering information.

(d)   	A complete equipment list indicating quantities and relevant catalogue numbers.

## 12.4 	Completion

The supply contract shall be regarded as incomplete until all tests have been conducted successfully and all drawings and manuals have been handed to the, Department

SECTION C20

# C.20  MOULDED-CASE CIRCUIT-BREAKERS

1.    	This section covers single or multi pole moulded case circuit breakers for use in power distribution systems, suitable for panel mounting, for ratings up to 1 000 A, 600 V. 50 Hz.

2.    	The circuit breakers shall comply with SANS 156.

3.    	The continuous current rating, trip rating and rupturing capacity shall be as specified.

4.    	The contacts shall be silver alloy and shall close with a high pressure wiping action.

5.    	Where specified, the circuit breaker shall be capable of accommodating factory fitted shunt trip or auxiliary contact units or similar equipment.

6.    	The operating handle shall provide clear indication of "ON", "OFF" and "TRIP" positions.

7.    	The mechanism shall be of the TRIP-FREE type preventing the unit from being held in the ON position under overload conditions.

8.    	All moulded case circuit breakers in a particular installation shall as far as is practical be supplied by a single manufacturer.

9.    	The incoming terminals of single pole miniature circuit breakers shall be suitable for connection to a common busbar.

10.   	The circuit breaker shall have a rating plate indicating the current rating, voltage rating and breaking capacity.

- Extension type operating handles shall be provided for units of 600 A rating and above.

SECTION C24

# C.24  EARTH LEAKAGE RELAYS

1.    	Earth leakage relays shall be single or three-phase units with a sensitivity of 30mA with associated circuit breaker or on-load switch for use on 220/250V single phase or 380/433 V three phase, 50 Hz, supplies.

2.    	The units shall be suitable for installation in switchboards in clip-in trays or bolted to the chassis.

3.    	The earth leakage relay shall function on the current balance principle and shall comply with SANS 767 as amended, and shall bear the SANS mark. Integral test facilities shall be incorporated in the unit.

4.    	Circuit breakers with trip coils used integrally with earth leakage units (two pole for single phase units and three pole for three phase units) shall comply with SANS 156.

5.    	On-load switches used integrally with earth leakage units (two pole for single-phase units and three pole for three phase units) shall comply with SANS 60497.

6.    	The fault current rating of the unit shall be 2,5kA or 5kA as required, when tested in accordance with SANS 156.

SECTION C30

# C.30  TIME SWITCHES AND PHOTOCELLS

1.    	Time switches shall be of single-pole type, suitable for 220/250 V systems, with contacts rated for the duty to be performed with a minimum rating of 15A. Contacts shall be of high quality material, e.g. silver-plated or solid silver.

2.    	The clock shall be driven by a self-starting, hysteresis synchronous motor, keeping accurate mains time. All clocks shall be controlled by an electrically wound escapement providing the main spring with a minimum of 15 hours reserve in case of a power failure. The main spring shall be kept fully wound without the use of slipping clutch devices that may wear and fall out of adjustment.

3.    	The main spring shall have a minimum of 15 hours reserve under full load and if fully discharged, shall be completely rewound within 15 minutes of the restoration of power.

4.    	An external manual bypass switch shall be provided to permit the circuit to be switched "ON" or "OFF" manually without affecting the operation of the time switch.

5.    	The time switch shall have a 24 hour dial, with day and night indication, that can be set to switch in 30 minute steps. The dial shall be fitted with 48 tappets corresponding to 48 change-over operations in a 24 hour period.

6.     	The time switch shall be fitted with a day omission dial comprising a total of 14 tappets which can be set to switch in 12 hour steps.

7.     	The time switch shall be housed in a dust-tight moulded plastic or metal case, consisting of a plastic clip-on front cover and a moulded plastic or metal base. Time switches to be used for surface mounting on walls shall be provided with a suitably positioned 20mm conduit knock-out.

PHOTOCELLS

# 1.    	GENERAL

1.1    	The switches shall be used for the control of street lights and shall be provided with switch contacts able to carry at least 5 A. The current during no-load conditions may not exceed 50 mA.

  - The units shall be suitable for 240 V + 6%. 50Hz. single-phase alternating current.

# 2.	CONSTRUCTION

2.1    	The units shall be weather and vibration resistant as they are to be mounted on top of streetlight luminaires. The design shall be of such a nature that the units will be able to withstand both hail damage and damage by stone-throwers. If the units do not meet with these requirements, separate wire screens shall be provided for this purpose.

2.2    	The units shall be provided with a standard NEMA plug and socket. The socket shall have a bracket for mounting on a pole.

2.3    	All components shall be treated to be corrosion resistant.

# 3.    	OPERATING CONDITIONS

3.1    	The units shall be suitable for operating under dusty conditions between temperatures of -5 EC and 55 EC.

# 4.    	TECHNICAL REQUIREMENTS

4.1	units shall switch on when the light intensity drops to 15 lux + 20% and shall switch off when the light intensity again reaches 40 lux + 20%.

4.2	When the unit is in the "on" position there must be a delay of one minute if it were to switch off in the case of a sudden increase in the light intensity.

SECTION C31

# C.31  CONTACTORS

1.	Contactors shall be of the open or totally enclosed, triple- or double-pole, electromechanically operated, air-break type suitable for 380/433 V or 220/250 V supplies and shall comply with SANS 1092.

2.    	Contactors shall have the following characteristics:

(a)	Enclosed coil easily replaceable.

(b)	A permanent air gap in the magnetic circuit to prevent sticky operation.

(c)	Provision for quick and simple inspection of contacts.

(d)	Clearly marked main and auxiliary terminals.

3.    	All parts shall be accessible from the front.

4.    	Contactors which are not located in switchboards shall be housed in enclosures which comply with IP 54 of IEC 144.

5.    	The current rating of the contactor shall be as specified for the circuit with a switching duty in accordance with the SANS 1092 or IEC 158-1, utilisation category ACI for lighting and power circuits and utilisation category AC3 for motor starting.

6.    	In addition to the required current carrying capacity and switching duty of a contactor, the contactor chosen for a particular application shall be rated for the maximum through fault current allowed by the back-up protection devices at the point where the contactor is installed. Careful co-ordination of short circuit devices shall take place.

7.    	All laminations of the magnetic system of the contactor shall be tightly clamped. Noisy contactors will not be accepted.

8.    	Non-current-carrying metallic parts shall be solidly interconnected and a common screwed earth terminal shall be provided. The contactor shall be earthed to the switchboard earth bar.

9.    	Latched contactors shall be provided with a trip coil and a closing coil. The contactor shall remain closed after de-energising the closing coil and shall only trip on energising the trip coil.

10.   	Contactor operating coils shall have a voltage rating as required by the control circuitry and shall have limits of operation and temperature rise as specified in Clause 7.5 and Table IV of IEC 158-1. Latched contactors shall be capable of being tripped at 50% of the rated coil voltage.

11.   	Contactors for normal/standby changeover circuits shall be electrically and mechanically interlocked. Contactors in star-delta starters shall be electrically interlocked.

12.	Contactors with provision to add auxiliary contacts and convert auxiliary contacts on site are preferred. Contactors with permanently fixed auxiliary contacts shall have at least 1 x N/0 and 1 x N/C spare auxiliary contacts in addition to the contacts specified or control purposes and in addition to contacts required for self-holding operations or economy resistances. Where the number of auxiliary contacts required is greater than the number of contacts that can be accommodated on the contactor, an auxiliary relay or additional contactor shall be provided to supply the additional contacts.

13.   	It shall be possible to replace main contacts without disconnecting wiring.

14.   	Auxiliary contacts shall be capable of making, carrying continuously and breaking 6A at 230V AC, unity power factor for contactors used on 380-433/220-250 V systems.

15.   	Auxiliary contact functions required e.g. "lazy" contacts late-make, late-break, make-before-break, etc. shall be inherent in the contact design. Under no circumstances may these functions be improvised by bending contacts, loading contacts, etc. These functions shall be available in all contactors.

16.   	Spare auxiliary contacts shall be wired to numbered terminal strips in the switchboard and shall appear on the switchboard drawings.

17.    	All contactors on a specific project shall be from a standard range of one single manufacturer, unless specified to the contrary.

SECTION C33

# C.33  INDOOR SURGE ARRESTORS

1.    	Surge arrestors shall comply with the requirements of SANS 61643 or VDE 0675.

2.    	Surge arrestors shall be suitable for installation at altitudes of up to 1800m above sea level.

3.    	The unit shall be contained within a thermoplastic or cast resin housing and all internal components shall be fully sealed in.

4.    	The unit shall be supplied complete with a galvanised steel mounting bracket for convenient mounting onto the metalwork or tray of a switchboard.

5.    	Alternatively, the unit shall be of the type which can be mounted into the clip-tray of a switchboard.

6.    	Surge arrestors shall be provided in all cases where a switchboard is supplied directly from an overhead line.

7.    	In other cases, surge arrestors, if required, will be specified in the Detail Technical Specification.

SECTION C34

# C.34  WORKMANSHIP OF STAFF AND CERTIFICATE OF COMPLIANCE

1.    	Except in the case of electrical installations supplied by a single phase electricity supply at the point of supply, an accredited person shall exercise general control over all work being carried out.

2.    	The workmanship shall be of the highest standard abd to the satisfaction of SARS.

3.    	All substandard work, on indication by SARS inspectors, shall be rectified by and at the expense of the Contractor.

4.    	On completion of the service, a certificate of compliance must be issued to SARS’s representative/Agent in terms of the Occupational Health and Safety Act (Act 85 of 1993)