## Slide 1
PROJECT NUMBER 4973
SARS – RISSIK STREET, JOHANNESBURG
ROOF REPAIR INVESTIGATION
Notes: <number>

## Slide 2
GROUND FLOOR – COURTYARD
Required work:
Outlet servicing – wet services consultant
Partial Screed where ponding occurs
COURTYARD
COURTYARD

## Slide 3
GROUND FLOOR – COURTYARD
Required:
Counter flashing on coping details
Low maintenance window cill “Uni-Flashing” solution
COPING
WINDOW CILL

## Slide 4
7TH FLOOR – ROOF TERRACE
Required:
Counter flashing on coping details
Counter flashing up onto parapet wall
CRACKED BRITTLE WATERPROOFING
COVES PEELING

## Slide 5
7TH FLOOR – ROOF TERRACE
Required:
Maintenance on outlets
Counter flashing seals on cracks
DRAINAGE OUTLET
CRACKED PARAPET

## Slide 6
CONCRETE ROOF AND GUTTER
Required:
Strip and remove loose stone
To be re-torched and painted silver
STONE COVERED CONCRETE ROOF
GUTTERS BLOCKED WITH LOOSE STONE

## Slide 7
CONCRETE ROOF PARAPET WALLS
Required:
Seal all parapet walls
WATER SEEPAGE IN PARAPET WALLS
WATER SEEPAGE IN WALLS

## Slide 8
ROOF SHEETING
Required:
Re-paint roof sheets and check for leaks in gutters
Clear debris
Re-paint where necessary
RUSTED METAL ROOF SHEETS
GUTTERS

## Slide 9
ROOF GUTTERS AND FASCIA
Required:
Re-paint all fascia
Fix onto and make good
GUTTERS AND FASCIA
GUTTERS AND FASCIA